## modbus-map
Category | Location | Asset Name | Signal Name | Shown on SEL Control screen? | Description | Message Type | MODBUS Type | Function Code | MODBUS Register Start Address | MODBUS Register Stop Address | Register Count | Data Type | Writable | Variation | Engineering Units | Scale / State | Comments
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_ActivePower_VAL | Yes | Active power (MW) from field for GEN1 | Operation Message | Input Register | 0x04 | 30001 | 30002 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10016 | 10016 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_ActivePower_VAL | Yes | Active power (MW) from field for GEN2 | Operation Message | Input Register | 0x04 | 30036 | 30037 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10037 | 10037 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_ActivePower_VAL | Yes | Active power (MW) from field for GEN3 | Operation Message | Input Register | 0x04 | 30071 | 30072 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10058 | 10058 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_ActivePower_VAL | Yes | Active power (MW) from field for GEN4 | Operation Message | Input Register | 0x04 | 30106 | 30107 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10079 | 10079 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_ActivePower_VAL | Yes | Active power (MW) from field for GEN5 | Operation Message | Input Register | 0x04 | 30141 | 30142 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10100 | 10100 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_ActivePower_VAL | Yes | Active power (MW) from field for GEN6 | Operation Message | Input Register | 0x04 | 30176 | 30177 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10121 | 10121 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_ActivePower_VAL | Yes | Active power (MW) from field for GEN7 | Operation Message | Input Register | 0x04 | 30211 | 30212 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10142 | 10142 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_ActivePower_VAL | Yes | Active power (MW) from field for GEN8 | Operation Message | Input Register | 0x04 | 30246 | 30247 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10163 | 10163 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_ActivePower_VAL | Yes | Active power (MW) from field for GEN9 | Operation Message | Input Register | 0x04 | 30281 | 30282 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10184 | 10184 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_ActivePower_VAL | Yes | Active power (MW) from field for GEN10 | Operation Message | Input Register | 0x04 | 30316 | 30317 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10205 | 10205 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_ActivePower_VAL | Yes | Active power (MW) from field for GEN11 | Operation Message | Input Register | 0x04 | 30351 | 30352 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10226 | 10226 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_ActivePower_VAL | Yes | Active power (MW) from field for GEN12 | Operation Message | Input Register | 0x04 | 30386 | 30387 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10247 | 10247 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_ActivePower_VAL | Yes | Active power (MW) from field for GEN13 | Operation Message | Input Register | 0x04 | 30421 | 30422 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10268 | 10268 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_ActivePower_VAL | Yes | Active power (MW) from field for GEN14 | Operation Message | Input Register | 0x04 | 30456 | 30457 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10289 | 10289 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_ActivePower_VAL | Yes | Active power (MW) from field for GEN15 | Operation Message | Input Register | 0x04 | 30491 | 30492 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10310 | 10310 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_ActivePower_VAL | Yes | Active power (MW) from field for GEN16 | Operation Message | Input Register | 0x04 | 30526 | 30527 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10331 | 10331 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_ActivePower_VAL | Yes | Active power (MW) from field for GEN17 | Operation Message | Input Register | 0x04 | 30561 | 30562 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10352 | 10352 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_ActivePower_VAL | Yes | Active power (MW) from field for GEN18 | Operation Message | Input Register | 0x04 | 30596 | 30597 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10373 | 10373 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_ActivePower_VAL | Yes | Active power (MW) from field for GEN19 | Operation Message | Input Register | 0x04 | 30631 | 30632 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10394 | 10394 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_ActivePower_VAL | Yes | Active power (MW) from field for GEN20 | Operation Message | Input Register | 0x04 | 30666 | 30667 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10415 | 10415 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_ActivePower_VAL | Yes | Active power (MW) from field for GEN21 | Operation Message | Input Register | 0x04 | 30701 | 30702 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10436 | 10436 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_ActivePower_VAL | Yes | Active power (MW) from field for GEN22 | Operation Message | Input Register | 0x04 | 30736 | 30737 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10457 | 10457 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_ActivePower_VAL | Yes | Active power (MW) from field for GEN23 | Operation Message | Input Register | 0x04 | 30771 | 30772 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10478 | 10478 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_ActivePower_VAL | Yes | Active power (MW) from field for GEN24 | Operation Message | Input Register | 0x04 | 30806 | 30807 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10499 | 10499 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_ActivePower_VAL | Yes | Active power (MW) from field for GEN25 | Operation Message | Input Register | 0x04 | 30841 | 30842 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10520 | 10520 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_ActivePower_VAL | Yes | Active power (MW) from field for GEN26 | Operation Message | Input Register | 0x04 | 30876 | 30877 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10541 | 10541 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_ActivePower_VAL | Yes | Active power (MW) from field for GEN27 | Operation Message | Input Register | 0x04 | 30911 | 30912 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10562 | 10562 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_ActivePower_VAL | Yes | Active power (MW) from field for GEN28 | Operation Message | Input Register | 0x04 | 30946 | 30947 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10583 | 10583 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_ActivePower_VAL | Yes | Active power (MW) from field for GEN29 | Operation Message | Input Register | 0x04 | 30981 | 30982 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10604 | 10604 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_ActivePower_VAL | Yes | Active power (MW) from field for GEN30 | Operation Message | Input Register | 0x04 | 31016 | 31017 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10625 | 10625 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_ActivePower_VAL | Yes | Active power (MW) from field for GEN31 | Operation Message | Input Register | 0x04 | 31051 | 31052 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10646 | 10646 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_ActivePower_VAL | Yes | Active power (MW) from field for GEN32 | Operation Message | Input Register | 0x04 | 31086 | 31087 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10667 | 10667 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_ActivePower_VAL | Yes | Active power (MW) from field for GEN33 | Operation Message | Input Register | 0x04 | 31121 | 31122 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10688 | 10688 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_ActivePower_VAL | Yes | Active power (MW) from field for GEN34 | Operation Message | Input Register | 0x04 | 31156 | 31157 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10709 | 10709 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_ActivePower_VAL | Yes | Active power (MW) from field for GEN35 | Operation Message | Input Register | 0x04 | 31191 | 31192 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10730 | 10730 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_ActivePower_VAL | Yes | Active power (MW) from field for GEN36 | Operation Message | Input Register | 0x04 | 31226 | 31227 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10751 | 10751 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_ActivePower_VAL | Yes | Active power (MW) from field for GEN37 | Operation Message | Input Register | 0x04 | 31261 | 31262 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10772 | 10772 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_ActivePower_VAL | Yes | Active power (MW) from field for GEN38 | Operation Message | Input Register | 0x04 | 31296 | 31297 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10793 | 10793 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_ActivePower_VAL | Yes | Active power (MW) from field for GEN39 | Operation Message | Input Register | 0x04 | 31331 | 31332 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10814 | 10814 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_ActivePower_VAL | Yes | Active power (MW) from field for GEN40 | Operation Message | Input Register | 0x04 | 31366 | 31367 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10835 | 10835 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_ActivePower_VAL | Yes | Active power (MW) from field for GEN41 | Operation Message | Input Register | 0x04 | 31401 | 31402 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10856 | 10856 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_ActivePower_VAL | Yes | Active power (MW) from field for GEN42 | Operation Message | Input Register | 0x04 | 31436 | 31437 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10877 | 10877 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_ActivePower_VAL | Yes | Active power (MW) from field for GEN43 | Operation Message | Input Register | 0x04 | 31471 | 31472 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10898 | 10898 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_ActivePower_VAL | Yes | Active power (MW) from field for GEN44 | Operation Message | Input Register | 0x04 | 31506 | 31507 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10919 | 10919 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_ActivePower_VAL | Yes | Active power (MW) from field for GEN45 | Operation Message | Input Register | 0x04 | 31541 | 31542 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10940 | 10940 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_ActivePower_VAL | Yes | Active power (MW) from field for GEN46 | Operation Message | Input Register | 0x04 | 31576 | 31577 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW |  | Failure Message | Discrete Input | 0x02 | 10961 | 10961 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10005 | 10005 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10026 | 10026 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10047 | 10047 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10068 | 10068 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10089 | 10089 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10110 | 10110 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10131 | 10131 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10152 | 10152 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10173 | 10173 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10194 | 10194 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10215 | 10215 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10236 | 10236 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10257 | 10257 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10278 | 10278 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10299 | 10299 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10320 | 10320 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10341 | 10341 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10362 | 10362 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10383 | 10383 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10404 | 10404 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10425 | 10425 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10446 | 10446 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10467 | 10467 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10488 | 10488 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10509 | 10509 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10530 | 10530 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10551 | 10551 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10572 | 10572 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10593 | 10593 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10614 | 10614 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10635 | 10635 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10656 | 10656 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10677 | 10677 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10698 | 10698 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10719 | 10719 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10740 | 10740 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10761 | 10761 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10782 | 10782 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10803 | 10803 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10824 | 10824 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10845 | 10845 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10866 | 10866 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10887 | 10887 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10908 | 10908 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10929 | 10929 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MW setpoint when controller is master | Failure Message | Discrete Input | 0x02 | 10950 | 10950 | 1 | Boolean | No | N/A | 1 = High, 0 = Low | 0=normal, 1=alarm state
Blackstart Sequence | N/A | N/A | BS_BlackoutRecoveryAlarm_STAT | Yes | Alarm status for blackout recovery sequence | Failure Message | Discrete Input | 0x02 | 10971 | 10971 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Blackstart Sequence | N/A | N/A | BS_BlackstartSequenceAlarm_STAT | Yes | Alarm status for blackstart sequence | Failure Message | Discrete Input | 0x02 | 10972 | 10972 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | N/A | N/A | GMS_PriorityNewGroup_CMD | Yes | Assign prepared running priority value to selected gen as part of a new unique priority group | Command | Coil | 0x05 | 432 | 432 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | N/A | N/A | GMS_PriorityAddToGroup_CMD | Yes | Assign prepared running priority value to selected gen as part of an existing priority group | Command | Coil | 0x05 | 431 | 431 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | N/A | N/A | GMS_PriorityInhibit_CMD | Yes | Assign selected gen a running priority of 0 to be inhibited in GMS | Command | Coil | 0x05 | 433 | 433 | 1 | Boolean | Yes | N/A | Pulse | N/A
Blackstart Sequence | N/A | N/A | BS_ActionFailed_STAT | Yes | Blackstart action failed HMI indication | Alarm Message | Discrete Input | 0x02 | 10967 | 10967 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Blackstart Sequence | N/A | N/A | BS_ReadyToAcceptLoad_STAT | Yes | Blackstart EDG ready to accept load indication | Operation Message | Discrete Input | 0x02 | 10970 | 10970 | 1 | Boolean | No | N/A | Latch
Blackstart Sequence | N/A | N/A | BS_ShutdownActive_STAT | Yes | Blackstart EDG shutdown active indication | Operation Message | Discrete Input | 0x02 | 10969 | 10969 | 1 | Boolean | No | N/A | Latch
Blackstart Sequence | N/A | N/A | BS_MasterEnabled_STAT | Yes | Blackstart enabled HMI indication | Operation Message | Discrete Input | 0x02 | 10968 | 10968 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Blackstart Sequence | N/A | N/A | BS_Abort_CMD | Yes | Blackstart operator abort command | Command | Coil | 0x05 | 368 | 368 | 1 | Boolean | Yes | N/A | Pulse | N/A
Blackstart Sequence | N/A | N/A | BS_Continue_CMD | Yes | Blackstart operator continue command | Command | Coil | 0x05 | 370 | 370 | 1 | Boolean | Yes | N/A | Pulse | N/A
Blackstart Sequence | N/A | N/A | BS_Restart_CMD | Yes | Blackstart operator restart command | Command | Coil | 0x05 | 369 | 369 | 1 | Boolean | Yes | N/A | Pulse | N/A
Blackstart Sequence | N/A | N/A | BS_Start_CMD | Yes | Blackstart operator start command | Command | Coil | 0x05 | 371 | 371 | 1 | Boolean | Yes | N/A | Pulse | N/A
Blackstart Sequence | N/A | N/A | BS_Stop_CMD | Yes | Blackstart operator stop command | Command | Coil | 0x05 | 372 | 372 | 1 | Boolean | Yes | N/A | Pulse | N/A
Blackstart Sequence | N/A | N/A | AUXABusDead_STAT | Yes | Blackstart screen status for E-House bus de-energized | Operation Message | Discrete Input | 0x02 | 11199 | 11199 | 1 | Boolean | No | N/A | N/A | N/A
Blackstart Sequence | N/A | N/A | MainBusDead_STAT | Yes | Blackstart screen status for overhead bus de-energized | Operation Message | Discrete Input | 0x02 | 11198 | 11198 | 1 | Boolean | No | N/A | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_TimeBeforeNextAction_VAL | Yes | Blackstart sequence current step timer |  | Input Register | 0x04 | 2979 | 2979 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_IEDs_CommHealthy_STAT | Yes | Blackstart sequence permissive checking for healthy comms with E-House IEDs | Operation Message | Discrete Input | 0x02 | 11197 | 11197 | 1 | Boolean | No | N/A | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_ReadytoInitiate_STAT | Yes | Blackstart sequence permissive for ready to be initiated by operator | Operation Message | Discrete Input | 0x02 | 11200 | 11200 | 1 | Boolean | No | N/A | N/A | N/A
Blackstart Sequence | Auxiliary E-House | N/A | BS_Step_ClsTieEM1_VAL | Yes | Blackstart sequence status for step: close Tie and EM1 breakers |  | Input Register | 0x04 | 2978 | 2978 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-01 | CB_101_01_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 616 | 616 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-02 | CB_101_02_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 617 | 617 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-03 | CB_101_03_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 618 | 618 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-04 | CB_101_04_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 619 | 619 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-05 | CB_101_05_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 620 | 620 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-06 | CB_101_06_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 621 | 621 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-07 | CB_101_07_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 622 | 622 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-08 | CB_101_08_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 623 | 623 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-09 | CB_101_09_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 624 | 624 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-10 | CB_101_10_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 625 | 625 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-11 | CB_101_11_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 626 | 626 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-01 | CB_102_01_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 627 | 627 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-02 | CB_102_02_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 628 | 628 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-03 | CB_102_03_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 629 | 629 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-04 | CB_102_04_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 630 | 630 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-05 | CB_102_05_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 631 | 631 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-06 | CB_102_06_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 632 | 632 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-07 | CB_102_07_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 633 | 633 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-08 | CB_102_08_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 634 | 634 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-09 | CB_102_09_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 635 | 635 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-10 | CB_102_10_PPLA_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 636 | 636 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-01 | CB_101_01_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 637 | 637 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-02 | CB_101_02_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 638 | 638 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-03 | CB_101_03_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 639 | 639 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-04 | CB_101_04_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 640 | 640 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-05 | CB_101_05_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 641 | 641 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-06 | CB_101_06_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 642 | 642 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-07 | CB_101_07_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 643 | 643 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-08 | CB_101_08_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 644 | 644 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-09 | CB_101_09_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 645 | 645 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-10 | CB_101_10_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 646 | 646 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-11 | CB_101_11_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 647 | 647 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-01 | CB_102_01_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 648 | 648 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-02 | CB_102_02_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 649 | 649 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-03 | CB_102_03_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 650 | 650 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-04 | CB_102_04_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 651 | 651 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-05 | CB_102_05_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 652 | 652 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-06 | CB_102_06_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 653 | 653 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-07 | CB_102_07_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 654 | 654 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-08 | CB_102_08_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 655 | 655 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-09 | CB_102_09_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 656 | 656 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-10 | CB_102_10_PPLB_Close_CMD | No | Breaker Close Command | Command | Coil | 0x05 | 657 | 657 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-01 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-02 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-03 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-04 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-05 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-06 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-07 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-08 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-09 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-10 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-11 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-01 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-02 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-03 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-04 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-05 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-06 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-07 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-08 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-09 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-10 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-01 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-02 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-03 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-04 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-05 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-06 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-07 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-08 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-09 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-10 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-11 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-01 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-02 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-03 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-04 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-05 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-06 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-07 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-08 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-09 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-10 | TBD | No | Breaker Close Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus A) | AUX-A-F1 | AUX_F1A_Close_CMD | No | Breaker Close Command for AUX-A-F1 | Command | Coil | 0x05 | 549 | 549 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus A) | AUX-A-F2 | AUX_F2A_Close_CMD | No | Breaker Close Command for AUX-A-F2 | Command | Coil | 0x05 | 551 | 551 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus A) | AUX-A-F3 | AUX_F3A_Close_CMD | No | Breaker Close Command for AUX-A-F3 | Command | Coil | 0x05 | 553 | 553 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus B) | AUX-B-F1 | AUX_F1B_Close_CMD | No | Breaker Close Command for AUX-B-F1 | Command | Coil | 0x05 | 555 | 555 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus B) | AUX-B-F2 | AUX_F2B_Close_CMD | No | Breaker Close Command for AUX-B-F2 | Command | Coil | 0x05 | 557 | 557 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus B) | AUX-B-F3 | AUX_F3B_Close_CMD | No | Breaker Close Command for AUX-B-F3 | Command | Coil | 0x05 | 559 | 559 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | EM-1 | AUX_EM1_Close_CMD | No | Breaker Close Command for EM-1 | Command | Coil | 0x05 | 541 | 541 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-01 | LOAD_FCB1_Close_CMD | No | Breaker Close Command for FCB-01 | Command | Coil | 0x05 | 561 | 561 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-02 | LOAD_FCB2_Close_CMD | No | Breaker Close Command for FCB-02 | Command | Coil | 0x05 | 563 | 563 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-03 | LOAD_FCB3_Close_CMD | No | Breaker Close Command for FCB-03 | Command | Coil | 0x05 | 565 | 565 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-04 | LOAD_FCB4_Close_CMD | No | Breaker Close Command for FCB-04 | Command | Coil | 0x05 | 567 | 567 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-05 | LOAD_FCB5_Close_CMD | No | Breaker Close Command for FCB-05 | Command | Coil | 0x05 | 569 | 569 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GCB-01 | GCS_G1_BkrClose_CMD | No | Breaker close command for GCB-01 | Command | Coil | 0x05 | 4 | 4 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GCB-02 | GCS_G2_BkrClose_CMD | No | Breaker close command for GCB-02 | Command | Coil | 0x05 | 12 | 12 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GCB-03 | GCS_G3_BkrClose_CMD | No | Breaker close command for GCB-03 | Command | Coil | 0x05 | 20 | 20 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GCB-04 | GCS_G4_BkrClose_CMD | No | Breaker close command for GCB-04 | Command | Coil | 0x05 | 28 | 28 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GCB-05 | GCS_G5_BkrClose_CMD | No | Breaker close command for GCB-05 | Command | Coil | 0x05 | 36 | 36 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GCB-06 | GCS_G6_BkrClose_CMD | No | Breaker close command for GCB-06 | Command | Coil | 0x05 | 44 | 44 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GCB-07 | GCS_G7_BkrClose_CMD | No | Breaker close command for GCB-07 | Command | Coil | 0x05 | 52 | 52 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GCB-08 | GCS_G8_BkrClose_CMD | No | Breaker close command for GCB-08 | Command | Coil | 0x05 | 60 | 60 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GCB-09 | GCS_G9_BkrClose_CMD | No | Breaker close command for GCB-09 | Command | Coil | 0x05 | 68 | 68 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GCB-10 | GCS_G10_BkrClose_CMD | No | Breaker close command for GCB-10 | Command | Coil | 0x05 | 76 | 76 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GCB-11 | GCS_G11_BkrClose_CMD | No | Breaker close command for GCB-11 | Command | Coil | 0x05 | 84 | 84 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GCB-12 | GCS_G12_BkrClose_CMD | No | Breaker close command for GCB-12 | Command | Coil | 0x05 | 92 | 92 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GCB-13 | GCS_G13_BkrClose_CMD | No | Breaker close command for GCB-13 | Command | Coil | 0x05 | 100 | 100 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GCB-14 | GCS_G14_BkrClose_CMD | No | Breaker close command for GCB-14 | Command | Coil | 0x05 | 108 | 108 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GCB-15 | GCS_G15_BkrClose_CMD | No | Breaker close command for GCB-15 | Command | Coil | 0x05 | 116 | 116 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GCB-16 | GCS_G16_BkrClose_CMD | No | Breaker close command for GCB-16 | Command | Coil | 0x05 | 124 | 124 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GCB-17 | GCS_G17_BkrClose_CMD | No | Breaker close command for GCB-17 | Command | Coil | 0x05 | 132 | 132 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GCB-18 | GCS_G18_BkrClose_CMD | No | Breaker close command for GCB-18 | Command | Coil | 0x05 | 140 | 140 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GCB-19 | GCS_G19_BkrClose_CMD | No | Breaker close command for GCB-19 | Command | Coil | 0x05 | 148 | 148 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GCB-20 | GCS_G20_BkrClose_CMD | No | Breaker close command for GCB-20 | Command | Coil | 0x05 | 156 | 156 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GCB-21 | GCS_G21_BkrClose_CMD | No | Breaker close command for GCB-21 | Command | Coil | 0x05 | 164 | 164 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GCB-22 | GCS_G22_BkrClose_CMD | No | Breaker close command for GCB-22 | Command | Coil | 0x05 | 172 | 172 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GCB-23 | GCS_G23_BkrClose_CMD | No | Breaker close command for GCB-23 | Command | Coil | 0x05 | 180 | 180 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GCB-24 | GCS_G24_BkrClose_CMD | No | Breaker close command for GCB-24 | Command | Coil | 0x05 | 188 | 188 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GCB-25 | GCS_G25_BkrClose_CMD | No | Breaker close command for GCB-25 | Command | Coil | 0x05 | 196 | 196 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GCB-26 | GCS_G26_BkrClose_CMD | No | Breaker close command for GCB-26 | Command | Coil | 0x05 | 204 | 204 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GCB-27 | GCS_G27_BkrClose_CMD | No | Breaker close command for GCB-27 | Command | Coil | 0x05 | 212 | 212 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GCB-28 | GCS_G28_BkrClose_CMD | No | Breaker close command for GCB-28 | Command | Coil | 0x05 | 220 | 220 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GCB-29 | GCS_G29_BkrClose_CMD | No | Breaker close command for GCB-29 | Command | Coil | 0x05 | 228 | 228 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GCB-30 | GCS_G30_BkrClose_CMD | No | Breaker close command for GCB-30 | Command | Coil | 0x05 | 236 | 236 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GCB-31 | GCS_G31_BkrClose_CMD | No | Breaker close command for GCB-31 | Command | Coil | 0x05 | 244 | 244 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GCB-32 | GCS_G32_BkrClose_CMD | No | Breaker close command for GCB-32 | Command | Coil | 0x05 | 252 | 252 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GCB-33 | GCS_G33_BkrClose_CMD | No | Breaker close command for GCB-33 | Command | Coil | 0x05 | 260 | 260 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GCB-34 | GCS_G34_BkrClose_CMD | No | Breaker close command for GCB-34 | Command | Coil | 0x05 | 268 | 268 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GCB-35 | GCS_G35_BkrClose_CMD | No | Breaker close command for GCB-35 | Command | Coil | 0x05 | 276 | 276 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GCB-36 | GCS_G36_BkrClose_CMD | No | Breaker close command for GCB-36 | Command | Coil | 0x05 | 284 | 284 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GCB-37 | GCS_G37_BkrClose_CMD | No | Breaker close command for GCB-37 | Command | Coil | 0x05 | 292 | 292 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GCB-38 | GCS_G38_BkrClose_CMD | No | Breaker close command for GCB-38 | Command | Coil | 0x05 | 300 | 300 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GCB-39 | GCS_G39_BkrClose_CMD | No | Breaker close command for GCB-39 | Command | Coil | 0x05 | 308 | 308 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GCB-40 | GCS_G40_BkrClose_CMD | No | Breaker close command for GCB-40 | Command | Coil | 0x05 | 316 | 316 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GCB-41 | GCS_G41_BkrClose_CMD | No | Breaker close command for GCB-41 | Command | Coil | 0x05 | 324 | 324 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GCB-42 | GCS_G42_BkrClose_CMD | No | Breaker close command for GCB-42 | Command | Coil | 0x05 | 332 | 332 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GCB-43 | GCS_G43_BkrClose_CMD | No | Breaker close command for GCB-43 | Command | Coil | 0x05 | 340 | 340 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GCB-44 | GCS_G44_BkrClose_CMD | No | Breaker close command for GCB-44 | Command | Coil | 0x05 | 348 | 348 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GCB-45 | GCS_G45_BkrClose_CMD | No | Breaker close command for GCB-45 | Command | Coil | 0x05 | 356 | 356 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GCB-46 | GCS_G46_BkrClose_CMD | No | Breaker close command for GCB-46 | Command | Coil | 0x05 | 364 | 364 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-1 | ICB-01 | ICB_G1_Close_CMD | No | Breaker Close Command for ICB-01 | Command | Coil | 0x05 | 439 | 439 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-1 | ICB-02 | ICB_G2_Close_CMD | No | Breaker Close Command for ICB-02 | Command | Coil | 0x05 | 441 | 441 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-1 | ICB-03 | ICB_G3_Close_CMD | No | Breaker Close Command for ICB-03 | Command | Coil | 0x05 | 443 | 443 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-1 | ICB-04 | ICB_G4_Close_CMD | No | Breaker Close Command for ICB-04 | Command | Coil | 0x05 | 445 | 445 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-2 | ICB-05 | ICB_G5_Close_CMD | No | Breaker Close Command for ICB-05 | Command | Coil | 0x05 | 447 | 447 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-2 | ICB-06 | ICB_G6_Close_CMD | No | Breaker Close Command for ICB-06 | Command | Coil | 0x05 | 449 | 449 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-2 | ICB-07 | ICB_G7_Close_CMD | No | Breaker Close Command for ICB-07 | Command | Coil | 0x05 | 451 | 451 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-2 | ICB-08 | ICB_G8_Close_CMD | No | Breaker Close Command for ICB-08 | Command | Coil | 0x05 | 453 | 453 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-3 | ICB-09 | ICB_G9_Close_CMD | No | Breaker Close Command for ICB-09 | Command | Coil | 0x05 | 455 | 455 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-3 | ICB-10 | ICB_G10_Close_CMD | No | Breaker Close Command for ICB-10 | Command | Coil | 0x05 | 457 | 457 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-3 | ICB-11 | ICB_G11_Close_CMD | No | Breaker Close Command for ICB-11 | Command | Coil | 0x05 | 459 | 459 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-3 | ICB-12 | ICB_G12_Close_CMD | No | Breaker Close Command for ICB-12 | Command | Coil | 0x05 | 461 | 461 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-4 | ICB-13 | ICB_G13_Close_CMD | No | Breaker Close Command for ICB-13 | Command | Coil | 0x05 | 463 | 463 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-4 | ICB-14 | ICB_G14_Close_CMD | No | Breaker Close Command for ICB-14 | Command | Coil | 0x05 | 465 | 465 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-4 | ICB-15 | ICB_G15_Close_CMD | No | Breaker Close Command for ICB-15 | Command | Coil | 0x05 | 467 | 467 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-4 | ICB-16 | ICB_G16_Close_CMD | No | Breaker Close Command for ICB-16 | Command | Coil | 0x05 | 469 | 469 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-5 | ICB-17 | ICB_G17_Close_CMD | No | Breaker Close Command for ICB-17 | Command | Coil | 0x05 | 471 | 471 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-5 | ICB-18 | ICB_G18_Close_CMD | No | Breaker Close Command for ICB-18 | Command | Coil | 0x05 | 473 | 473 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-5 | ICB-19 | ICB_G19_Close_CMD | No | Breaker Close Command for ICB-19 | Command | Coil | 0x05 | 475 | 475 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-5 | ICB-20 | ICB_G20_Close_CMD | No | Breaker Close Command for ICB-20 | Command | Coil | 0x05 | 477 | 477 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-6 | ICB-21 | ICB_G21_Close_CMD | No | Breaker Close Command for ICB-21 | Command | Coil | 0x05 | 479 | 479 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-6 | ICB-22 | ICB_G22_Close_CMD | No | Breaker Close Command for ICB-22 | Command | Coil | 0x05 | 481 | 481 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-6 | ICB-23 | ICB_G23_Close_CMD | No | Breaker Close Command for ICB-23 | Command | Coil | 0x05 | 483 | 483 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-6 | ICB-24 | ICB_G24_Close_CMD | No | Breaker Close Command for ICB-24 | Command | Coil | 0x05 | 485 | 485 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-7 | ICB-25 | ICB_G25_Close_CMD | No | Breaker Close Command for ICB-25 | Command | Coil | 0x05 | 487 | 487 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-7 | ICB-26 | ICB_G26_Close_CMD | No | Breaker Close Command for ICB-26 | Command | Coil | 0x05 | 489 | 489 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-7 | ICB-27 | ICB_G27_Close_CMD | No | Breaker Close Command for ICB-27 | Command | Coil | 0x05 | 491 | 491 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-7 | ICB-28 | ICB_G28_Close_CMD | No | Breaker Close Command for ICB-28 | Command | Coil | 0x05 | 493 | 493 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-8 | ICB-29 | ICB_G29_Close_CMD | No | Breaker Close Command for ICB-29 | Command | Coil | 0x05 | 495 | 495 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-8 | ICB-30 | ICB_G30_Close_CMD | No | Breaker Close Command for ICB-30 | Command | Coil | 0x05 | 497 | 497 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-8 | ICB-31 | ICB_G31_Close_CMD | No | Breaker Close Command for ICB-31 | Command | Coil | 0x05 | 499 | 499 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-8 | ICB-32 | ICB_G32_Close_CMD | No | Breaker Close Command for ICB-32 | Command | Coil | 0x05 | 501 | 501 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-9 | ICB-33 | ICB_G33_Close_CMD | No | Breaker Close Command for ICB-33 | Command | Coil | 0x05 | 503 | 503 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-9 | ICB-34 | ICB_G34_Close_CMD | No | Breaker Close Command for ICB-34 | Command | Coil | 0x05 | 505 | 505 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-9 | ICB-35 | ICB_G35_Close_CMD | No | Breaker Close Command for ICB-35 | Command | Coil | 0x05 | 507 | 507 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-9 | ICB-36 | ICB_G36_Close_CMD | No | Breaker Close Command for ICB-36 | Command | Coil | 0x05 | 509 | 509 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-10 | ICB-37 | ICB_G37_Close_CMD | No | Breaker Close Command for ICB-37 | Command | Coil | 0x05 | 511 | 511 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-10 | ICB-38 | ICB_G38_Close_CMD | No | Breaker Close Command for ICB-38 | Command | Coil | 0x05 | 513 | 513 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-10 | ICB-39 | ICB_G39_Close_CMD | No | Breaker Close Command for ICB-39 | Command | Coil | 0x05 | 515 | 515 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-10 | ICB-40 | ICB_G40_Close_CMD | No | Breaker Close Command for ICB-40 | Command | Coil | 0x05 | 517 | 517 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-11 | ICB-41 | ICB_G41_Close_CMD | No | Breaker Close Command for ICB-41 | Command | Coil | 0x05 | 519 | 519 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-11 | ICB-42 | ICB_G42_Close_CMD | No | Breaker Close Command for ICB-42 | Command | Coil | 0x05 | 521 | 521 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-11 | ICB-43 | ICB_G43_Close_CMD | No | Breaker Close Command for ICB-43 | Command | Coil | 0x05 | 523 | 523 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-11 | ICB-44 | ICB_G44_Close_CMD | No | Breaker Close Command for ICB-44 | Command | Coil | 0x05 | 525 | 525 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-12 | ICB-45 | ICB_G45_Close_CMD | No | Breaker Close Command for ICB-45 | Command | Coil | 0x05 | 527 | 527 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-12 | ICB-46 | ICB_G46_Close_CMD | No | Breaker Close Command for ICB-46 | Command | Coil | 0x05 | 529 | 529 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | ICB-47 | ICB_XFMRAUX1_Close_CMD | No | Breaker Close Command for ICB-47 | Command | Coil | 0x05 | 531 | 531 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | ICB-48 | ICB_XFMRAUX2_Close_CMD | No | Breaker Close Command for ICB-48 | Command | Coil | 0x05 | 533 | 533 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | ICB-49 | ICB_S1_Close_CMD | No | Breaker Close Command for ICB-49 | Command | Coil | 0x05 | 535 | 535 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | ICB-50 | ICB_S2_Close_CMD | No | Breaker Close Command for ICB-50 | Command | Coil | 0x05 | 537 | 537 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | Main-1 | AUX_MAIN1_Close_CMD | No | Breaker Close Command for Main-1 | Command | Coil | 0x05 | 543 | 543 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | Main-2 | AUX_MAIN2_Close_CMD | No | Breaker Close Command for Main-2 | Command | Coil | 0x05 | 545 | 545 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | SC1-15kV-BKR | SC_S1_Close_CMD | No | Breaker Close Command for SC1-15kV-BKR | Command | Coil | 0x05 | 435 | 435 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | SC2-15kV-BKR | SC_S2_Close_CMD | No | Breaker Close Command for SC2-15kV-BKR | Command | Coil | 0x05 | 437 | 437 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | Tie | AUX_TIE_Close_CMD | No | Breaker Close Command for Tie | Command | Coil | 0x05 | 547 | 547 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-01 | CB_101_01_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 574 | 574 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-02 | CB_101_02_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 575 | 575 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-03 | CB_101_03_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 576 | 576 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-04 | CB_101_04_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 577 | 577 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-05 | CB_101_05_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 578 | 578 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-06 | CB_101_06_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 579 | 579 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-07 | CB_101_07_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 580 | 580 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-08 | CB_101_08_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 581 | 581 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-09 | CB_101_09_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 582 | 582 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-10 | CB_101_10_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 583 | 583 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-11 | CB_101_11_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 584 | 584 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-01 | CB_102_01_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 585 | 585 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-02 | CB_102_02_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 586 | 586 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-03 | CB_102_03_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 587 | 587 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-04 | CB_102_04_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 588 | 588 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-05 | CB_102_05_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 589 | 589 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-06 | CB_102_06_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 590 | 590 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-07 | CB_102_07_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 591 | 591 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-08 | CB_102_08_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 592 | 592 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-09 | CB_102_09_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 593 | 593 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-10 | CB_102_10_PPLA_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 594 | 594 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-01 | CB_101_01_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 595 | 595 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-02 | CB_101_02_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 596 | 596 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-03 | CB_101_03_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 597 | 597 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-04 | CB_101_04_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 598 | 598 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-05 | CB_101_05_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 599 | 599 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-06 | CB_101_06_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 600 | 600 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-07 | CB_101_07_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 601 | 601 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-08 | CB_101_08_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 602 | 602 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-09 | CB_101_09_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 603 | 603 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-10 | CB_101_10_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 604 | 604 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-11 | CB_101_11_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 605 | 605 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-01 | CB_102_01_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 606 | 606 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-02 | CB_102_02_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 607 | 607 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-03 | CB_102_03_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 608 | 608 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-04 | CB_102_04_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 609 | 609 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-05 | CB_102_05_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 610 | 610 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-06 | CB_102_06_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 611 | 611 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-07 | CB_102_07_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 612 | 612 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-08 | CB_102_08_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 613 | 613 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-09 | CB_102_09_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 614 | 614 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-10 | CB_102_10_PPLB_Open_CMD | No | Breaker Open Command | Command | Coil | 0x05 | 615 | 615 | 1 | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-01 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-02 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-03 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-04 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-05 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-06 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-07 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-08 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-09 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-10 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-101-11 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-01 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-02 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-03 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-04 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-05 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-06 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-07 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-08 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-09 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-A | CB-102-10 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-01 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-02 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-03 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-04 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-05 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-06 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-07 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-08 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-09 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-10 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-101-11 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-01 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-02 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-03 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-04 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-05 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-06 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-07 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-08 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-09 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | E-House PPL-B | CB-102-10 | TBD | No | Breaker Open Command | Command | Coil | 0x05 |  |  |  | Boolean | Yes | N/A | N/A | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus A) | AUX-A-F1 | AUX_F1A_Open_CMD | No | Breaker Open Command for AUX-A-F1 | Command | Coil | 0x05 | 548 | 548 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus A) | AUX-A-F2 | AUX_F2A_Open_CMD | No | Breaker Open Command for AUX-A-F2 | Command | Coil | 0x05 | 550 | 550 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus A) | AUX-A-F3 | AUX_F3A_Open_CMD | No | Breaker Open Command for AUX-A-F3 | Command | Coil | 0x05 | 552 | 552 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus B) | AUX-B-F1 | AUX_F1B_Open_CMD | No | Breaker Open Command for AUX-B-F1 | Command | Coil | 0x05 | 554 | 554 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus B) | AUX-B-F2 | AUX_F2B_Open_CMD | No | Breaker Open Command for AUX-B-F2 | Command | Coil | 0x05 | 556 | 556 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus B) | AUX-B-F3 | AUX_F3B_Open_CMD | No | Breaker Open Command for AUX-B-F3 | Command | Coil | 0x05 | 558 | 558 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | EM-1 | AUX_EM1_Open_CMD | No | Breaker Open Command for EM-1 | Command | Coil | 0x05 | 540 | 540 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-01 | LOAD_FCB1_Open_CMD | No | Breaker Open Command for FCB-01 | Command | Coil | 0x05 | 560 | 560 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-02 | LOAD_FCB2_Open_CMD | No | Breaker Open Command for FCB-02 | Command | Coil | 0x05 | 562 | 562 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-03 | LOAD_FCB3_Open_CMD | No | Breaker Open Command for FCB-03 | Command | Coil | 0x05 | 564 | 564 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-04 | LOAD_FCB4_Open_CMD | No | Breaker Open Command for FCB-04 | Command | Coil | 0x05 | 566 | 566 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Feeders | FCB-05 | LOAD_FCB5_Open_CMD | No | Breaker Open Command for FCB-05 | Command | Coil | 0x05 | 568 | 568 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GCB-01 | GCS_G1_BkrOpen_CMD | No | Breaker open command for GCB-01 | Command | Coil | 0x05 | 3 | 3 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GCB-02 | GCS_G2_BkrOpen_CMD | No | Breaker open command for GCB-02 | Command | Coil | 0x05 | 11 | 11 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GCB-03 | GCS_G3_BkrOpen_CMD | No | Breaker open command for GCB-03 | Command | Coil | 0x05 | 19 | 19 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GCB-04 | GCS_G4_BkrOpen_CMD | No | Breaker open command for GCB-04 | Command | Coil | 0x05 | 27 | 27 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GCB-05 | GCS_G5_BkrOpen_CMD | No | Breaker open command for GCB-05 | Command | Coil | 0x05 | 35 | 35 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GCB-06 | GCS_G6_BkrOpen_CMD | No | Breaker open command for GCB-06 | Command | Coil | 0x05 | 43 | 43 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GCB-07 | GCS_G7_BkrOpen_CMD | No | Breaker open command for GCB-07 | Command | Coil | 0x05 | 51 | 51 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GCB-08 | GCS_G8_BkrOpen_CMD | No | Breaker open command for GCB-08 | Command | Coil | 0x05 | 59 | 59 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GCB-09 | GCS_G9_BkrOpen_CMD | No | Breaker open command for GCB-09 | Command | Coil | 0x05 | 67 | 67 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GCB-10 | GCS_G10_BkrOpen_CMD | No | Breaker open command for GCB-10 | Command | Coil | 0x05 | 75 | 75 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GCB-11 | GCS_G11_BkrOpen_CMD | No | Breaker open command for GCB-11 | Command | Coil | 0x05 | 83 | 83 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GCB-12 | GCS_G12_BkrOpen_CMD | No | Breaker open command for GCB-12 | Command | Coil | 0x05 | 91 | 91 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GCB-13 | GCS_G13_BkrOpen_CMD | No | Breaker open command for GCB-13 | Command | Coil | 0x05 | 99 | 99 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GCB-14 | GCS_G14_BkrOpen_CMD | No | Breaker open command for GCB-14 | Command | Coil | 0x05 | 107 | 107 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GCB-15 | GCS_G15_BkrOpen_CMD | No | Breaker open command for GCB-15 | Command | Coil | 0x05 | 115 | 115 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GCB-16 | GCS_G16_BkrOpen_CMD | No | Breaker open command for GCB-16 | Command | Coil | 0x05 | 123 | 123 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GCB-17 | GCS_G17_BkrOpen_CMD | No | Breaker open command for GCB-17 | Command | Coil | 0x05 | 131 | 131 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GCB-18 | GCS_G18_BkrOpen_CMD | No | Breaker open command for GCB-18 | Command | Coil | 0x05 | 139 | 139 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GCB-19 | GCS_G19_BkrOpen_CMD | No | Breaker open command for GCB-19 | Command | Coil | 0x05 | 147 | 147 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GCB-20 | GCS_G20_BkrOpen_CMD | No | Breaker open command for GCB-20 | Command | Coil | 0x05 | 155 | 155 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GCB-21 | GCS_G21_BkrOpen_CMD | No | Breaker open command for GCB-21 | Command | Coil | 0x05 | 163 | 163 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GCB-22 | GCS_G22_BkrOpen_CMD | No | Breaker open command for GCB-22 | Command | Coil | 0x05 | 171 | 171 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GCB-23 | GCS_G23_BkrOpen_CMD | No | Breaker open command for GCB-23 | Command | Coil | 0x05 | 179 | 179 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GCB-24 | GCS_G24_BkrOpen_CMD | No | Breaker open command for GCB-24 | Command | Coil | 0x05 | 187 | 187 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GCB-25 | GCS_G25_BkrOpen_CMD | No | Breaker open command for GCB-25 | Command | Coil | 0x05 | 195 | 195 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GCB-26 | GCS_G26_BkrOpen_CMD | No | Breaker open command for GCB-26 | Command | Coil | 0x05 | 203 | 203 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GCB-27 | GCS_G27_BkrOpen_CMD | No | Breaker open command for GCB-27 | Command | Coil | 0x05 | 211 | 211 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GCB-28 | GCS_G28_BkrOpen_CMD | No | Breaker open command for GCB-28 | Command | Coil | 0x05 | 219 | 219 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GCB-29 | GCS_G29_BkrOpen_CMD | No | Breaker open command for GCB-29 | Command | Coil | 0x05 | 227 | 227 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GCB-30 | GCS_G30_BkrOpen_CMD | No | Breaker open command for GCB-30 | Command | Coil | 0x05 | 235 | 235 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GCB-31 | GCS_G31_BkrOpen_CMD | No | Breaker open command for GCB-31 | Command | Coil | 0x05 | 243 | 243 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GCB-32 | GCS_G32_BkrOpen_CMD | No | Breaker open command for GCB-32 | Command | Coil | 0x05 | 251 | 251 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GCB-33 | GCS_G33_BkrOpen_CMD | No | Breaker open command for GCB-33 | Command | Coil | 0x05 | 259 | 259 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GCB-34 | GCS_G34_BkrOpen_CMD | No | Breaker open command for GCB-34 | Command | Coil | 0x05 | 267 | 267 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GCB-35 | GCS_G35_BkrOpen_CMD | No | Breaker open command for GCB-35 | Command | Coil | 0x05 | 275 | 275 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GCB-36 | GCS_G36_BkrOpen_CMD | No | Breaker open command for GCB-36 | Command | Coil | 0x05 | 283 | 283 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GCB-37 | GCS_G37_BkrOpen_CMD | No | Breaker open command for GCB-37 | Command | Coil | 0x05 | 291 | 291 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GCB-38 | GCS_G38_BkrOpen_CMD | No | Breaker open command for GCB-38 | Command | Coil | 0x05 | 299 | 299 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GCB-39 | GCS_G39_BkrOpen_CMD | No | Breaker open command for GCB-39 | Command | Coil | 0x05 | 307 | 307 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GCB-40 | GCS_G40_BkrOpen_CMD | No | Breaker open command for GCB-40 | Command | Coil | 0x05 | 315 | 315 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GCB-41 | GCS_G41_BkrOpen_CMD | No | Breaker open command for GCB-41 | Command | Coil | 0x05 | 323 | 323 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GCB-42 | GCS_G42_BkrOpen_CMD | No | Breaker open command for GCB-42 | Command | Coil | 0x05 | 331 | 331 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GCB-43 | GCS_G43_BkrOpen_CMD | No | Breaker open command for GCB-43 | Command | Coil | 0x05 | 339 | 339 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GCB-44 | GCS_G44_BkrOpen_CMD | No | Breaker open command for GCB-44 | Command | Coil | 0x05 | 347 | 347 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GCB-45 | GCS_G45_BkrOpen_CMD | No | Breaker open command for GCB-45 | Command | Coil | 0x05 | 355 | 355 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GCB-46 | GCS_G46_BkrOpen_CMD | No | Breaker open command for GCB-46 | Command | Coil | 0x05 | 363 | 363 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-1 | ICB-01 | ICB_G1_Open_CMD | No | Breaker Open command for ICB-01 | Command | Coil | 0x05 | 438 | 438 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-1 | ICB-02 | ICB_G2_Open_CMD | No | Breaker Open command for ICB-02 | Command | Coil | 0x05 | 440 | 440 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-1 | ICB-03 | ICB_G3_Open_CMD | No | Breaker Open command for ICB-03 | Command | Coil | 0x05 | 442 | 442 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-1 | ICB-04 | ICB_G4_Open_CMD | No | Breaker Open command for ICB-04 | Command | Coil | 0x05 | 444 | 444 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-2 | ICB-05 | ICB_G5_Open_CMD | No | Breaker Open command for ICB-05 | Command | Coil | 0x05 | 446 | 446 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-2 | ICB-06 | ICB_G6_Open_CMD | No | Breaker Open command for ICB-06 | Command | Coil | 0x05 | 448 | 448 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-2 | ICB-07 | ICB_G7_Open_CMD | No | Breaker Open command for ICB-07 | Command | Coil | 0x05 | 450 | 450 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-2 | ICB-08 | ICB_G8_Open_CMD | No | Breaker Open command for ICB-08 | Command | Coil | 0x05 | 452 | 452 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-3 | ICB-09 | ICB_G9_Open_CMD | No | Breaker Open command for ICB-09 | Command | Coil | 0x05 | 454 | 454 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-3 | ICB-10 | ICB_G10_Open_CMD | No | Breaker Open command for ICB-10 | Command | Coil | 0x05 | 456 | 456 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-3 | ICB-11 | ICB_G11_Open_CMD | No | Breaker Open command for ICB-11 | Command | Coil | 0x05 | 458 | 458 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-3 | ICB-12 | ICB_G12_Open_CMD | No | Breaker Open command for ICB-12 | Command | Coil | 0x05 | 460 | 460 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-4 | ICB-13 | ICB_G13_Open_CMD | No | Breaker Open command for ICB-13 | Command | Coil | 0x05 | 462 | 462 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-4 | ICB-14 | ICB_G14_Open_CMD | No | Breaker Open command for ICB-14 | Command | Coil | 0x05 | 464 | 464 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-4 | ICB-15 | ICB_G15_Open_CMD | No | Breaker Open command for ICB-15 | Command | Coil | 0x05 | 466 | 466 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-4 | ICB-16 | ICB_G16_Open_CMD | No | Breaker Open command for ICB-16 | Command | Coil | 0x05 | 468 | 468 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-5 | ICB-17 | ICB_G17_Open_CMD | No | Breaker Open command for ICB-17 | Command | Coil | 0x05 | 470 | 470 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-5 | ICB-18 | ICB_G18_Open_CMD | No | Breaker Open command for ICB-18 | Command | Coil | 0x05 | 472 | 472 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-5 | ICB-19 | ICB_G19_Open_CMD | No | Breaker Open command for ICB-19 | Command | Coil | 0x05 | 474 | 474 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-5 | ICB-20 | ICB_G20_Open_CMD | No | Breaker Open command for ICB-20 | Command | Coil | 0x05 | 476 | 476 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-6 | ICB-21 | ICB_G21_Open_CMD | No | Breaker Open command for ICB-21 | Command | Coil | 0x05 | 478 | 478 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-6 | ICB-22 | ICB_G22_Open_CMD | No | Breaker Open command for ICB-22 | Command | Coil | 0x05 | 480 | 480 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-6 | ICB-23 | ICB_G23_Open_CMD | No | Breaker Open command for ICB-23 | Command | Coil | 0x05 | 482 | 482 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-6 | ICB-24 | ICB_G24_Open_CMD | No | Breaker Open command for ICB-24 | Command | Coil | 0x05 | 484 | 484 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-7 | ICB-25 | ICB_G25_Open_CMD | No | Breaker Open command for ICB-25 | Command | Coil | 0x05 | 486 | 486 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-7 | ICB-26 | ICB_G26_Open_CMD | No | Breaker Open command for ICB-26 | Command | Coil | 0x05 | 488 | 488 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-7 | ICB-27 | ICB_G27_Open_CMD | No | Breaker Open command for ICB-27 | Command | Coil | 0x05 | 490 | 490 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-7 | ICB-28 | ICB_G28_Open_CMD | No | Breaker Open command for ICB-28 | Command | Coil | 0x05 | 492 | 492 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-8 | ICB-29 | ICB_G29_Open_CMD | No | Breaker Open command for ICB-29 | Command | Coil | 0x05 | 494 | 494 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-8 | ICB-30 | ICB_G30_Open_CMD | No | Breaker Open command for ICB-30 | Command | Coil | 0x05 | 496 | 496 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-8 | ICB-31 | ICB_G31_Open_CMD | No | Breaker Open command for ICB-31 | Command | Coil | 0x05 | 498 | 498 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-8 | ICB-32 | ICB_G32_Open_CMD | No | Breaker Open command for ICB-32 | Command | Coil | 0x05 | 500 | 500 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-9 | ICB-33 | ICB_G33_Open_CMD | No | Breaker Open command for ICB-33 | Command | Coil | 0x05 | 502 | 502 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-9 | ICB-34 | ICB_G34_Open_CMD | No | Breaker Open command for ICB-34 | Command | Coil | 0x05 | 504 | 504 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-9 | ICB-35 | ICB_G35_Open_CMD | No | Breaker Open command for ICB-35 | Command | Coil | 0x05 | 506 | 506 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-9 | ICB-36 | ICB_G36_Open_CMD | No | Breaker Open command for ICB-36 | Command | Coil | 0x05 | 508 | 508 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-10 | ICB-37 | ICB_G37_Open_CMD | No | Breaker Open command for ICB-37 | Command | Coil | 0x05 | 510 | 510 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-10 | ICB-38 | ICB_G38_Open_CMD | No | Breaker Open command for ICB-38 | Command | Coil | 0x05 | 512 | 512 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-10 | ICB-39 | ICB_G39_Open_CMD | No | Breaker Open command for ICB-39 | Command | Coil | 0x05 | 514 | 514 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-10 | ICB-40 | ICB_G40_Open_CMD | No | Breaker Open command for ICB-40 | Command | Coil | 0x05 | 516 | 516 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-11 | ICB-41 | ICB_G41_Open_CMD | No | Breaker Open command for ICB-41 | Command | Coil | 0x05 | 518 | 518 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-11 | ICB-42 | ICB_G42_Open_CMD | No | Breaker Open command for ICB-42 | Command | Coil | 0x05 | 520 | 520 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-11 | ICB-43 | ICB_G43_Open_CMD | No | Breaker Open command for ICB-43 | Command | Coil | 0x05 | 522 | 522 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-11 | ICB-44 | ICB_G44_Open_CMD | No | Breaker Open command for ICB-44 | Command | Coil | 0x05 | 524 | 524 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-12 | ICB-45 | ICB_G45_Open_CMD | No | Breaker Open command for ICB-45 | Command | Coil | 0x05 | 526 | 526 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | ICB-45 | ICB_XFMRAUX1_Open_CMD | No | Breaker Open Command for ICB-45 | Command | Coil | 0x05 | 530 | 530 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | QPAC-12 | ICB-46 | ICB_G46_Open_CMD | No | Breaker Open command for ICB-46 | Command | Coil | 0x05 | 528 | 528 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | ICB-46 | ICB_XFMRAUX2_Open_CMD | No | Breaker Open Command for ICB-46 | Command | Coil | 0x05 | 532 | 532 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | ICB-47 | ICB_S1_Open_CMD | No | Breaker Open Command for ICB-47 | Command | Coil | 0x05 | 534 | 534 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | ICB-48 | ICB_S2_Open_CMD | No | Breaker Open Command for ICB-48 | Command | Coil | 0x05 | 536 | 536 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | Main-1 | AUX_MAIN1_Open_CMD | No | Breaker Open Command for Main-1 | Command | Coil | 0x05 | 542 | 542 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | Main-2 | AUX_MAIN2_Open_CMD | No | Breaker Open Command for Main-2 | Command | Coil | 0x05 | 544 | 544 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | SC1-15kV-BKR | SC_S1_Open_CMD | No | Breaker Open Command for SC1-15kV-BKR | Command | Coil | 0x05 | 434 | 434 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | SC2-15kV-BKR | SC_S2_Open_CMD | No | Breaker Open Command for SC2-15kV-BKR | Command | Coil | 0x05 | 436 | 436 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House | Tie | AUX_TIE_Open_CMD | No | Breaker Open Command for Tie | Command | Coil | 0x05 | 546 | 546 | 1 | Boolean | Yes | N/A | Pulse | N/A
Blackstart Sequence | Auxiliary E-House | EM-1 | AUX_EM1_BreakerStatus_VAL | Yes | Breaker status for Aux EM1; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32945 | 32945 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House (Bus A) | F1 | AUX_F1A_BreakerStatus_VAL | Yes | Breaker status for Aux F1A; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32954 | 32954 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House (Bus B) | F1 | AUX_F1B_BreakerStatus_VAL | Yes | Breaker status for Aux F1B; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32957 | 32957 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House (Bus A) | F2 | AUX_F2A_BreakerStatus_VAL | Yes | Breaker status for Aux F2A; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32955 | 32955 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House (Bus B) | F2 | AUX_F2B_BreakerStatus_VAL | Yes | Breaker status for Aux F2B; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32958 | 32958 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House (Bus A) | F3 | AUX_F3A_BreakerStatus_VAL | Yes | Breaker status for Aux F3A; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32956 | 32956 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House (Bus B) | F3 | AUX_F3B_BreakerStatus_VAL | Yes | Breaker status for Aux F3B; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32959 | 32959 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House | Main-1 | AUX_MAIN1_BreakerStatus_VAL | Yes | Breaker status for Aux MAIN1; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32946 | 32946 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House | Main-2 | AUX_MAIN2_BreakerStatus_VAL | Yes | Breaker status for Aux MAIN2; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32947 | 32947 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House | Tie | AUX_TIE_BreakerStatus_VAL | Yes | Breaker status for Aux TIE; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32948 | 32948 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House | unknown | BS_EDG_BreakerStatus_VAL | Yes | Breaker status for EDG BKR; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31632 | 31632 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | Feeders | FCB-01 | LOAD_FCB1_BreakerStatus_VAL | No | Breaker status for FCB-01; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32949 | 32949 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | Feeders | FCB-02 | LOAD_FCB2_BreakerStatus_VAL | No | Breaker status for FCB-02; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32950 | 32950 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | Feeders | FCB-03 | LOAD_FCB3_BreakerStatus_VAL | No | Breaker status for FCB-03; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32951 | 32951 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | Feeders | FCB-04 | LOAD_FCB4_BreakerStatus_VAL | No | Breaker status for FCB-04; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32952 | 32952 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | Feeders | FCB-05 | LOAD_FCB5_BreakerStatus_VAL | No | Breaker status for FCB-05; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32953 | 32953 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_BreakerStatus_VAL | Yes | Breaker status for GCB-1; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30013 | 30013 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_BreakerStatus_VAL | Yes | Breaker status for GCB-1; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30028 | 30028 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-3 | ICB-10 | AGC_G10_BreakerStatus_VAL | Yes | Breaker status for GCB-10; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30328 | 30328 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-3 | ICB-10 | VCS_G10_BreakerStatus_VAL | Yes | Breaker status for GCB-10; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30343 | 30343 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-3 | ICB-11 | AGC_G11_BreakerStatus_VAL | Yes | Breaker status for GCB-11; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30363 | 30363 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-3 | ICB-11 | VCS_G11_BreakerStatus_VAL | Yes | Breaker status for GCB-11; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30378 | 30378 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-3 | ICB-12 | AGC_G12_BreakerStatus_VAL | Yes | Breaker status for GCB-12; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30398 | 30398 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-3 | ICB-12 | VCS_G12_BreakerStatus_VAL | Yes | Breaker status for GCB-12; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30413 | 30413 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-4 | ICB-13 | AGC_G13_BreakerStatus_VAL | Yes | Breaker status for GCB-13; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30433 | 30433 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-4 | ICB-13 | VCS_G13_BreakerStatus_VAL | Yes | Breaker status for GCB-13; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30448 | 30448 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-4 | ICB-14 | AGC_G14_BreakerStatus_VAL | Yes | Breaker status for GCB-14; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30468 | 30468 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-4 | ICB-14 | VCS_G14_BreakerStatus_VAL | Yes | Breaker status for GCB-14; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30483 | 30483 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-4 | ICB-15 | AGC_G15_BreakerStatus_VAL | Yes | Breaker status for GCB-15; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30503 | 30503 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-4 | ICB-15 | VCS_G15_BreakerStatus_VAL | Yes | Breaker status for GCB-15; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30518 | 30518 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-4 | ICB-16 | AGC_G16_BreakerStatus_VAL | Yes | Breaker status for GCB-16; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30538 | 30538 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-4 | ICB-16 | VCS_G16_BreakerStatus_VAL | Yes | Breaker status for GCB-16; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30553 | 30553 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-5 | ICB-17 | AGC_G17_BreakerStatus_VAL | Yes | Breaker status for GCB-17; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30573 | 30573 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-5 | ICB-17 | VCS_G17_BreakerStatus_VAL | Yes | Breaker status for GCB-17; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30588 | 30588 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-5 | ICB-18 | AGC_G18_BreakerStatus_VAL | Yes | Breaker status for GCB-18; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30608 | 30608 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-5 | ICB-18 | VCS_G18_BreakerStatus_VAL | Yes | Breaker status for GCB-18; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30623 | 30623 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-5 | ICB-19 | AGC_G19_BreakerStatus_VAL | Yes | Breaker status for GCB-19; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30643 | 30643 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-5 | ICB-19 | VCS_G19_BreakerStatus_VAL | Yes | Breaker status for GCB-19; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30658 | 30658 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | ICB-02 | AGC_G2_BreakerStatus_VAL | Yes | Breaker status for GCB-2; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30048 | 30048 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-1 | ICB-02 | VCS_G2_BreakerStatus_VAL | Yes | Breaker status for GCB-2; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30063 | 30063 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-5 | ICB-20 | AGC_G20_BreakerStatus_VAL | Yes | Breaker status for GCB-20; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30678 | 30678 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-5 | ICB-20 | VCS_G20_BreakerStatus_VAL | Yes | Breaker status for GCB-20; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30693 | 30693 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-6 | ICB-21 | AGC_G21_BreakerStatus_VAL | Yes | Breaker status for GCB-21; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30713 | 30713 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-6 | ICB-21 | VCS_G21_BreakerStatus_VAL | Yes | Breaker status for GCB-21; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30728 | 30728 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-6 | ICB-22 | AGC_G22_BreakerStatus_VAL | Yes | Breaker status for GCB-22; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30748 | 30748 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-6 | ICB-22 | VCS_G22_BreakerStatus_VAL | Yes | Breaker status for GCB-22; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30763 | 30763 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-6 | ICB-23 | AGC_G23_BreakerStatus_VAL | Yes | Breaker status for GCB-23; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30783 | 30783 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-6 | ICB-23 | VCS_G23_BreakerStatus_VAL | Yes | Breaker status for GCB-23; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30798 | 30798 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-6 | ICB-24 | AGC_G24_BreakerStatus_VAL | Yes | Breaker status for GCB-24; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30818 | 30818 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-6 | ICB-24 | VCS_G24_BreakerStatus_VAL | Yes | Breaker status for GCB-24; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30833 | 30833 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-7 | ICB-25 | AGC_G25_BreakerStatus_VAL | Yes | Breaker status for GCB-25; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30853 | 30853 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-7 | ICB-25 | VCS_G25_BreakerStatus_VAL | Yes | Breaker status for GCB-25; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30868 | 30868 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-7 | ICB-26 | AGC_G26_BreakerStatus_VAL | Yes | Breaker status for GCB-26; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30888 | 30888 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-7 | ICB-26 | VCS_G26_BreakerStatus_VAL | Yes | Breaker status for GCB-26; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30903 | 30903 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-7 | ICB-27 | AGC_G27_BreakerStatus_VAL | Yes | Breaker status for GCB-27; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30923 | 30923 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-7 | ICB-27 | VCS_G27_BreakerStatus_VAL | Yes | Breaker status for GCB-27; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30938 | 30938 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-7 | ICB-28 | AGC_G28_BreakerStatus_VAL | Yes | Breaker status for GCB-28; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30958 | 30958 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-7 | ICB-28 | VCS_G28_BreakerStatus_VAL | Yes | Breaker status for GCB-28; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30973 | 30973 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-8 | ICB-29 | AGC_G29_BreakerStatus_VAL | Yes | Breaker status for GCB-29; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30993 | 30993 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-8 | ICB-29 | VCS_G29_BreakerStatus_VAL | Yes | Breaker status for GCB-29; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31008 | 31008 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | ICB-03 | AGC_G3_BreakerStatus_VAL | Yes | Breaker status for GCB-3; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30083 | 30083 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-1 | ICB-03 | VCS_G3_BreakerStatus_VAL | Yes | Breaker status for GCB-3; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30098 | 30098 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-8 | ICB-30 | AGC_G30_BreakerStatus_VAL | Yes | Breaker status for GCB-30; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31028 | 31028 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-8 | ICB-30 | VCS_G30_BreakerStatus_VAL | Yes | Breaker status for GCB-30; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31043 | 31043 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-8 | ICB-31 | AGC_G31_BreakerStatus_VAL | Yes | Breaker status for GCB-31; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31063 | 31063 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-8 | ICB-31 | VCS_G31_BreakerStatus_VAL | Yes | Breaker status for GCB-31; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31078 | 31078 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-8 | ICB-32 | AGC_G32_BreakerStatus_VAL | Yes | Breaker status for GCB-32; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31098 | 31098 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-8 | ICB-32 | VCS_G32_BreakerStatus_VAL | Yes | Breaker status for GCB-32; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31113 | 31113 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-9 | ICB-33 | AGC_G33_BreakerStatus_VAL | Yes | Breaker status for GCB-33; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31133 | 31133 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-9 | ICB-33 | VCS_G33_BreakerStatus_VAL | Yes | Breaker status for GCB-33; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31148 | 31148 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-9 | ICB-34 | AGC_G34_BreakerStatus_VAL | Yes | Breaker status for GCB-34; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31168 | 31168 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-9 | ICB-34 | VCS_G34_BreakerStatus_VAL | Yes | Breaker status for GCB-34; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31183 | 31183 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-9 | ICB-35 | AGC_G35_BreakerStatus_VAL | Yes | Breaker status for GCB-35; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31203 | 31203 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-9 | ICB-35 | VCS_G35_BreakerStatus_VAL | Yes | Breaker status for GCB-35; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31218 | 31218 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-9 | ICB-36 | AGC_G36_BreakerStatus_VAL | Yes | Breaker status for GCB-36; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31238 | 31238 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-9 | ICB-36 | VCS_G36_BreakerStatus_VAL | Yes | Breaker status for GCB-36; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31253 | 31253 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-10 | ICB-37 | AGC_G37_BreakerStatus_VAL | Yes | Breaker status for GCB-37; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31273 | 31273 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-10 | ICB-37 | VCS_G37_BreakerStatus_VAL | Yes | Breaker status for GCB-37; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31288 | 31288 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-10 | ICB-38 | AGC_G38_BreakerStatus_VAL | Yes | Breaker status for GCB-38; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31308 | 31308 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-10 | ICB-38 | VCS_G38_BreakerStatus_VAL | Yes | Breaker status for GCB-38; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31323 | 31323 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-10 | ICB-39 | AGC_G39_BreakerStatus_VAL | Yes | Breaker status for GCB-39; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31343 | 31343 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-10 | ICB-39 | VCS_G39_BreakerStatus_VAL | Yes | Breaker status for GCB-39; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31358 | 31358 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | ICB-04 | AGC_G4_BreakerStatus_VAL | Yes | Breaker status for GCB-4; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30118 | 30118 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-1 | ICB-04 | VCS_G4_BreakerStatus_VAL | Yes | Breaker status for GCB-4; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30133 | 30133 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-10 | ICB-40 | AGC_G40_BreakerStatus_VAL | Yes | Breaker status for GCB-40; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31378 | 31378 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-10 | ICB-40 | VCS_G40_BreakerStatus_VAL | Yes | Breaker status for GCB-40; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31393 | 31393 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-11 | ICB-41 | AGC_G41_BreakerStatus_VAL | Yes | Breaker status for GCB-41; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31413 | 31413 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-11 | ICB-41 | VCS_G41_BreakerStatus_VAL | Yes | Breaker status for GCB-41; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31428 | 31428 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-11 | ICB-42 | AGC_G42_BreakerStatus_VAL | Yes | Breaker status for GCB-42; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31448 | 31448 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-11 | ICB-42 | VCS_G42_BreakerStatus_VAL | Yes | Breaker status for GCB-42; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31463 | 31463 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-11 | ICB-43 | AGC_G43_BreakerStatus_VAL | Yes | Breaker status for GCB-43; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31483 | 31483 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-11 | ICB-43 | VCS_G43_BreakerStatus_VAL | Yes | Breaker status for GCB-43; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31498 | 31498 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-11 | ICB-44 | AGC_G44_BreakerStatus_VAL | Yes | Breaker status for GCB-44; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31518 | 31518 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-11 | ICB-44 | VCS_G44_BreakerStatus_VAL | Yes | Breaker status for GCB-44; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31533 | 31533 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-12 | ICB-45 | AGC_G45_BreakerStatus_VAL | Yes | Breaker status for GCB-45; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31553 | 31553 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-12 | ICB-45 | VCS_G45_BreakerStatus_VAL | Yes | Breaker status for GCB-45; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31568 | 31568 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-12 | ICB-46 | AGC_G46_BreakerStatus_VAL | Yes | Breaker status for GCB-46; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31588 | 31588 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-12 | ICB-46 | VCS_G46_BreakerStatus_VAL | Yes | Breaker status for GCB-46; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31603 | 31603 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-2 | ICB-05 | AGC_G5_BreakerStatus_VAL | Yes | Breaker status for GCB-5; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30153 | 30153 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-2 | ICB-05 | VCS_G5_BreakerStatus_VAL | Yes | Breaker status for GCB-5; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30168 | 30168 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-2 | ICB-06 | AGC_G6_BreakerStatus_VAL | Yes | Breaker status for GCB-6; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30188 | 30188 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-2 | ICB-06 | VCS_G6_BreakerStatus_VAL | Yes | Breaker status for GCB-6; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30203 | 30203 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-2 | ICB-07 | AGC_G7_BreakerStatus_VAL | Yes | Breaker status for GCB-7; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30223 | 30223 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-2 | ICB-07 | VCS_G7_BreakerStatus_VAL | Yes | Breaker status for GCB-7; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30238 | 30238 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-2 | ICB-08 | AGC_G8_BreakerStatus_VAL | Yes | Breaker status for GCB-8; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30258 | 30258 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-2 | ICB-08 | VCS_G8_BreakerStatus_VAL | Yes | Breaker status for GCB-8; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30273 | 30273 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-3 | ICB-09 | AGC_G9_BreakerStatus_VAL | Yes | Breaker status for GCB-9; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30293 | 30293 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-3 | ICB-09 | VCS_G9_BreakerStatus_VAL | Yes | Breaker status for GCB-9; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30308 | 30308 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-1 | ICB-01 | ICB_G1_BreakerStatus_VAL | No | Breaker status for ICB-01; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30035 | 30035 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-1 | ICB-02 | ICB_G2_BreakerStatus_VAL | No | Breaker status for ICB-02; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30070 | 30070 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-1 | ICB-03 | ICB_G3_BreakerStatus_VAL | No | Breaker status for ICB-03; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30105 | 30105 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-1 | ICB-04 | ICB_G4_BreakerStatus_VAL | No | Breaker status for ICB-04; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30140 | 30140 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-2 | ICB-05 | ICB_G5_BreakerStatus_VAL | No | Breaker status for ICB-05; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30175 | 30175 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-2 | ICB-06 | ICB_G6_BreakerStatus_VAL | No | Breaker status for ICB-06; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30210 | 30210 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-2 | ICB-07 | ICB_G7_BreakerStatus_VAL | No | Breaker status for ICB-07; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30245 | 30245 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-2 | ICB-08 | ICB_G8_BreakerStatus_VAL | No | Breaker status for ICB-08; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30280 | 30280 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-3 | ICB-09 | ICB_G9_BreakerStatus_VAL | No | Breaker status for ICB-09; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30315 | 30315 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-3 | ICB-10 | ICB_G10_BreakerStatus_VAL | No | Breaker status for ICB-10; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30350 | 30350 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-3 | ICB-11 | ICB_G11_BreakerStatus_VAL | No | Breaker status for ICB-11; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30385 | 30385 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-3 | ICB-12 | ICB_G12_BreakerStatus_VAL | No | Breaker status for ICB-12; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30420 | 30420 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-4 | ICB-13 | ICB_G13_BreakerStatus_VAL | No | Breaker status for ICB-13; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30455 | 30455 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-4 | ICB-14 | ICB_G14_BreakerStatus_VAL | No | Breaker status for ICB-14; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30490 | 30490 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-4 | ICB-15 | ICB_G15_BreakerStatus_VAL | No | Breaker status for ICB-15; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30525 | 30525 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-4 | ICB-16 | ICB_G16_BreakerStatus_VAL | No | Breaker status for ICB-16; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30560 | 30560 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-5 | ICB-17 | ICB_G17_BreakerStatus_VAL | No | Breaker status for ICB-17; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30595 | 30595 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-5 | ICB-18 | ICB_G18_BreakerStatus_VAL | No | Breaker status for ICB-18; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30630 | 30630 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-5 | ICB-19 | ICB_G19_BreakerStatus_VAL | No | Breaker status for ICB-19; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30665 | 30665 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-5 | ICB-20 | ICB_G20_BreakerStatus_VAL | No | Breaker status for ICB-20; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30700 | 30700 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-6 | ICB-21 | ICB_G21_BreakerStatus_VAL | No | Breaker status for ICB-21; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30735 | 30735 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-6 | ICB-22 | ICB_G22_BreakerStatus_VAL | No | Breaker status for ICB-22; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30770 | 30770 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-6 | ICB-23 | ICB_G23_BreakerStatus_VAL | No | Breaker status for ICB-23; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30805 | 30805 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-6 | ICB-24 | ICB_G24_BreakerStatus_VAL | No | Breaker status for ICB-24; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30840 | 30840 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-7 | ICB-25 | ICB_G25_BreakerStatus_VAL | No | Breaker status for ICB-25; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30875 | 30875 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-7 | ICB-26 | ICB_G26_BreakerStatus_VAL | No | Breaker status for ICB-26; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30910 | 30910 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-7 | ICB-27 | ICB_G27_BreakerStatus_VAL | No | Breaker status for ICB-27; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30945 | 30945 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-7 | ICB-28 | ICB_G28_BreakerStatus_VAL | No | Breaker status for ICB-28; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 30980 | 30980 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-8 | ICB-29 | ICB_G29_BreakerStatus_VAL | No | Breaker status for ICB-29; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31015 | 31015 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-8 | ICB-30 | ICB_G30_BreakerStatus_VAL | No | Breaker status for ICB-30; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31050 | 31050 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-8 | ICB-31 | ICB_G31_BreakerStatus_VAL | No | Breaker status for ICB-31; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31085 | 31085 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-8 | ICB-32 | ICB_G32_BreakerStatus_VAL | No | Breaker status for ICB-32; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31120 | 31120 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-9 | ICB-33 | ICB_G33_BreakerStatus_VAL | No | Breaker status for ICB-33; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31155 | 31155 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-9 | ICB-34 | ICB_G34_BreakerStatus_VAL | No | Breaker status for ICB-34; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31190 | 31190 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-9 | ICB-35 | ICB_G35_BreakerStatus_VAL | No | Breaker status for ICB-35; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31225 | 31225 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-9 | ICB-36 | ICB_G36_BreakerStatus_VAL | No | Breaker status for ICB-36; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31260 | 31260 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-10 | ICB-37 | ICB_G37_BreakerStatus_VAL | No | Breaker status for ICB-37; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31295 | 31295 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-10 | ICB-38 | ICB_G38_BreakerStatus_VAL | No | Breaker status for ICB-38; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31330 | 31330 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-10 | ICB-39 | ICB_G39_BreakerStatus_VAL | No | Breaker status for ICB-39; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31365 | 31365 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-10 | ICB-40 | ICB_G40_BreakerStatus_VAL | No | Breaker status for ICB-40; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31400 | 31400 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-11 | ICB-41 | ICB_G41_BreakerStatus_VAL | No | Breaker status for ICB-41; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31435 | 31435 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-11 | ICB-42 | ICB_G42_BreakerStatus_VAL | No | Breaker status for ICB-42; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31470 | 31470 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-11 | ICB-43 | ICB_G43_BreakerStatus_VAL | No | Breaker status for ICB-43; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31505 | 31505 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-11 | ICB-44 | ICB_G44_BreakerStatus_VAL | No | Breaker status for ICB-44; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 31540 | 31540 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House | ICB-47 | ICB_XFMRAUX1_BreakerStatus_VAL | Yes | Breaker status for ICB-45; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32939 | 32939 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House | ICB-48 | ICB_XFMRAUX2_BreakerStatus_VAL | Yes | Breaker status for ICB-46; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32940 | 32940 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | SYNCON | ICB-49 | ICB_SC1_BreakerStatus_VAL | No | Breaker status for ICB-47; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32941 | 32941 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | SYNCON | ICB-50 | ICB_SC2_BreakerStatus_VAL | No | Breaker status for ICB-48; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=binary alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32942 | 32942 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | SYNCON | SC1-15kV-BKR | SC_S1_BreakerStatus_VAL | No | Breaker status for SC1-15kV-BKR; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32943 | 32943 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | SYNCON | SC2-15kV-BKR | SC_S2_BreakerStatus_VAL | No | Breaker status for SC2-15kV-BKR; 0=open, 1=closed, 2=comm alarm, 3=TOC, 10=Binary Alarm, 11=local, 12=Analog Alarm, 13=invalid status | Operation Message | Input Register | 0x04 | 32944 | 32944 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Network Overview Screen | QPAC-1 | N/A | FEP_Q1A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 10997 | 10997 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-2 | N/A | FEP_Q2A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 10998 | 10998 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-3 | N/A | FEP_Q3A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 10999 | 10999 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-4 | N/A | FEP_Q4A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11000 | 11000 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-5 | N/A | FEP_Q5A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11001 | 11001 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-6 | N/A | FEP_Q6A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11002 | 11002 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-7 | N/A | FEP_Q7A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11003 | 11003 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-8 | N/A | FEP_Q8A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11004 | 11004 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-9 | N/A | FEP_Q9A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11005 | 11005 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-10 | N/A | FEP_Q10A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11006 | 11006 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-11 | N/A | FEP_Q11A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11007 | 11007 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-12 | N/A | FEP_Q12A_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11008 | 11008 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-1 | N/A | FEP_Q1B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11033 | 11033 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-2 | N/A | FEP_Q2B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11034 | 11034 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-3 | N/A | FEP_Q3B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11035 | 11035 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-4 | N/A | FEP_Q4B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11036 | 11036 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-5 | N/A | FEP_Q5B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11037 | 11037 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-6 | N/A | FEP_Q6B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11038 | 11038 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-7 | N/A | FEP_Q7B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11039 | 11039 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-8 | N/A | FEP_Q8B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11040 | 11040 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-9 | N/A | FEP_Q9B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11041 | 11041 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-10 | N/A | FEP_Q10B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11042 | 11042 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-11 | N/A | FEP_Q11B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11043 | 11043 | 1 | Boolean | No | N/A | Latch
Network Overview Screen | QPAC-12 | N/A | FEP_Q12B_CommissioningBit_STAT | Yes | Commissioning Isolation Bit |  | Discrete Input | 0x02 | 11044 | 11044 | 1 | Boolean | No | N/A | Latch
N/A | N/A | GCSA | GCSA_BootupComplete_STAT | No | Controller A bootup complete status, used to determine which controller is master Controller B uses the same address | Operation Message | Discrete Input | 0x02 | 11345 | 11345 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | SPARE | No | Created in map but not in use (SPARE) | Control Setpoint | Holding Register | 0x10 | 40601 | 40602 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
N/A | N/A | N/A | SPARE | No | Created in map but not in use (SPARE) | Control Setpoint | Holding Register | 0x10 | 40603 | 40604 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
N/A | N/A | N/A | SPARE | No | Created in map but not in use (SPARE) | Control Setpoint | Holding Register | 0x10 | 40615 | 40616 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
N/A | N/A | N/A | SPARE | No | Created in map but not in use (SPARE) | Control Setpoint | Holding Register | 0x06 | 40617 | 40617 | 1 | Int | Yes | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN1 | Operation Message | Input Register | 0x04 | 30024 | 30025 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN10 | Operation Message | Input Register | 0x04 | 30339 | 30340 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN11 | Operation Message | Input Register | 0x04 | 30374 | 30375 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN12 | Operation Message | Input Register | 0x04 | 30409 | 30410 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN13 | Operation Message | Input Register | 0x04 | 30444 | 30445 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN14 | Operation Message | Input Register | 0x04 | 30479 | 30480 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN15 | Operation Message | Input Register | 0x04 | 30514 | 30515 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN16 | Operation Message | Input Register | 0x04 | 30549 | 30550 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN17 | Operation Message | Input Register | 0x04 | 30584 | 30585 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN18 | Operation Message | Input Register | 0x04 | 30619 | 30620 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN19 | Operation Message | Input Register | 0x04 | 30654 | 30655 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN2 | Operation Message | Input Register | 0x04 | 30059 | 30060 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN20 | Operation Message | Input Register | 0x04 | 30689 | 30690 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN21 | Operation Message | Input Register | 0x04 | 30724 | 30725 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN22 | Operation Message | Input Register | 0x04 | 30759 | 30760 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN23 | Operation Message | Input Register | 0x04 | 30794 | 30795 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN24 | Operation Message | Input Register | 0x04 | 30829 | 30830 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN25 | Operation Message | Input Register | 0x04 | 30864 | 30865 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN26 | Operation Message | Input Register | 0x04 | 30899 | 30900 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN27 | Operation Message | Input Register | 0x04 | 30934 | 30935 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN28 | Operation Message | Input Register | 0x04 | 30969 | 30970 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN29 | Operation Message | Input Register | 0x04 | 31004 | 31005 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN3 | Operation Message | Input Register | 0x04 | 30094 | 30095 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN30 | Operation Message | Input Register | 0x04 | 31039 | 31040 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN31 | Operation Message | Input Register | 0x04 | 31074 | 31075 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN32 | Operation Message | Input Register | 0x04 | 31109 | 31110 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN33 | Operation Message | Input Register | 0x04 | 31144 | 31145 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN34 | Operation Message | Input Register | 0x04 | 31179 | 31180 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN35 | Operation Message | Input Register | 0x04 | 31214 | 31215 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN36 | Operation Message | Input Register | 0x04 | 31249 | 31250 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN37 | Operation Message | Input Register | 0x04 | 31284 | 31285 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN38 | Operation Message | Input Register | 0x04 | 31319 | 31320 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN39 | Operation Message | Input Register | 0x04 | 31354 | 31355 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN4 | Operation Message | Input Register | 0x04 | 30129 | 30130 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN40 | Operation Message | Input Register | 0x04 | 31389 | 31390 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN41 | Operation Message | Input Register | 0x04 | 31424 | 31425 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN42 | Operation Message | Input Register | 0x04 | 31459 | 31460 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN43 | Operation Message | Input Register | 0x04 | 31494 | 31495 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN44 | Operation Message | Input Register | 0x04 | 31529 | 31530 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN45 | Operation Message | Input Register | 0x04 | 31564 | 31565 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN46 | Operation Message | Input Register | 0x04 | 31599 | 31600 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN5 | Operation Message | Input Register | 0x04 | 30164 | 30165 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN6 | Operation Message | Input Register | 0x04 | 30199 | 30200 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN7 | Operation Message | Input Register | 0x04 | 30234 | 30235 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN8 | Operation Message | Input Register | 0x04 | 30269 | 30270 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_UpperRegLimit_VAL | Yes | Current MVAR upper regulation limit in controller for GEN9 | Operation Message | Input Register | 0x04 | 30304 | 30305 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN1 | Operation Message | Input Register | 0x04 | 30007 | 30008 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN10 | Operation Message | Input Register | 0x04 | 30322 | 30323 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN11 | Operation Message | Input Register | 0x04 | 30357 | 30358 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN12 | Operation Message | Input Register | 0x04 | 30392 | 30393 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN13 | Operation Message | Input Register | 0x04 | 30427 | 30428 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN14 | Operation Message | Input Register | 0x04 | 30462 | 30463 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN15 | Operation Message | Input Register | 0x04 | 30497 | 30498 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN16 | Operation Message | Input Register | 0x04 | 30532 | 30533 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN17 | Operation Message | Input Register | 0x04 | 30567 | 30568 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN18 | Operation Message | Input Register | 0x04 | 30602 | 30603 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN19 | Operation Message | Input Register | 0x04 | 30637 | 30638 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN2 | Operation Message | Input Register | 0x04 | 30042 | 30043 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN20 | Operation Message | Input Register | 0x04 | 30672 | 30673 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN21 | Operation Message | Input Register | 0x04 | 30707 | 30708 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN22 | Operation Message | Input Register | 0x04 | 30742 | 30743 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN23 | Operation Message | Input Register | 0x04 | 30777 | 30778 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN24 | Operation Message | Input Register | 0x04 | 30812 | 30813 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN25 | Operation Message | Input Register | 0x04 | 30847 | 30848 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN26 | Operation Message | Input Register | 0x04 | 30882 | 30883 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN27 | Operation Message | Input Register | 0x04 | 30917 | 30918 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN28 | Operation Message | Input Register | 0x04 | 30952 | 30953 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN29 | Operation Message | Input Register | 0x04 | 30987 | 30988 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN3 | Operation Message | Input Register | 0x04 | 30077 | 30078 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN30 | Operation Message | Input Register | 0x04 | 31022 | 31023 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN31 | Operation Message | Input Register | 0x04 | 31057 | 31058 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN32 | Operation Message | Input Register | 0x04 | 31092 | 31093 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN33 | Operation Message | Input Register | 0x04 | 31127 | 31128 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN34 | Operation Message | Input Register | 0x04 | 31162 | 31163 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN35 | Operation Message | Input Register | 0x04 | 31197 | 31198 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN36 | Operation Message | Input Register | 0x04 | 31232 | 31233 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN37 | Operation Message | Input Register | 0x04 | 31267 | 31268 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN38 | Operation Message | Input Register | 0x04 | 31302 | 31303 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN39 | Operation Message | Input Register | 0x04 | 31337 | 31338 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN4 | Operation Message | Input Register | 0x04 | 30112 | 30113 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN40 | Operation Message | Input Register | 0x04 | 31372 | 31373 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN41 | Operation Message | Input Register | 0x04 | 31407 | 31408 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN42 | Operation Message | Input Register | 0x04 | 31442 | 31443 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN43 | Operation Message | Input Register | 0x04 | 31477 | 31478 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN44 | Operation Message | Input Register | 0x04 | 31512 | 31513 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN45 | Operation Message | Input Register | 0x04 | 31547 | 31548 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN46 | Operation Message | Input Register | 0x04 | 31582 | 31583 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN5 | Operation Message | Input Register | 0x04 | 30147 | 30148 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN6 | Operation Message | Input Register | 0x04 | 30182 | 30183 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN7 | Operation Message | Input Register | 0x04 | 30217 | 30218 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN8 | Operation Message | Input Register | 0x04 | 30252 | 30253 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_LowerRegLimit_VAL | Yes | Current MW lower regulation limit in controller for GEN9 | Operation Message | Input Register | 0x04 | 30287 | 30288 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN1 | Operation Message | Input Register | 0x04 | 30009 | 30010 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN10 | Operation Message | Input Register | 0x04 | 30324 | 30325 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN11 | Operation Message | Input Register | 0x04 | 30359 | 30360 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN12 | Operation Message | Input Register | 0x04 | 30394 | 30395 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN13 | Operation Message | Input Register | 0x04 | 30429 | 30430 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN14 | Operation Message | Input Register | 0x04 | 30464 | 30465 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN15 | Operation Message | Input Register | 0x04 | 30499 | 30500 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN16 | Operation Message | Input Register | 0x04 | 30534 | 30535 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN17 | Operation Message | Input Register | 0x04 | 30569 | 30570 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN18 | Operation Message | Input Register | 0x04 | 30604 | 30605 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN19 | Operation Message | Input Register | 0x04 | 30639 | 30640 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN2 | Operation Message | Input Register | 0x04 | 30044 | 30045 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN20 | Operation Message | Input Register | 0x04 | 30674 | 30675 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN21 | Operation Message | Input Register | 0x04 | 30709 | 30710 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN22 | Operation Message | Input Register | 0x04 | 30744 | 30745 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN23 | Operation Message | Input Register | 0x04 | 30779 | 30780 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN24 | Operation Message | Input Register | 0x04 | 30814 | 30815 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN25 | Operation Message | Input Register | 0x04 | 30849 | 30850 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN26 | Operation Message | Input Register | 0x04 | 30884 | 30885 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN27 | Operation Message | Input Register | 0x04 | 30919 | 30920 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN28 | Operation Message | Input Register | 0x04 | 30954 | 30955 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN29 | Operation Message | Input Register | 0x04 | 30989 | 30990 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN3 | Operation Message | Input Register | 0x04 | 30079 | 30080 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN30 | Operation Message | Input Register | 0x04 | 31024 | 31025 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN31 | Operation Message | Input Register | 0x04 | 31059 | 31060 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN32 | Operation Message | Input Register | 0x04 | 31094 | 31095 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN33 | Operation Message | Input Register | 0x04 | 31129 | 31130 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN34 | Operation Message | Input Register | 0x04 | 31164 | 31165 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN35 | Operation Message | Input Register | 0x04 | 31199 | 31200 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN36 | Operation Message | Input Register | 0x04 | 31234 | 31235 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN37 | Operation Message | Input Register | 0x04 | 31269 | 31270 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN38 | Operation Message | Input Register | 0x04 | 31304 | 31305 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN39 | Operation Message | Input Register | 0x04 | 31339 | 31340 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN4 | Operation Message | Input Register | 0x04 | 30114 | 30115 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN40 | Operation Message | Input Register | 0x04 | 31374 | 31375 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN41 | Operation Message | Input Register | 0x04 | 31409 | 31410 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN42 | Operation Message | Input Register | 0x04 | 31444 | 31445 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN43 | Operation Message | Input Register | 0x04 | 31479 | 31480 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN44 | Operation Message | Input Register | 0x04 | 31514 | 31515 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN45 | Operation Message | Input Register | 0x04 | 31549 | 31550 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN46 | Operation Message | Input Register | 0x04 | 31584 | 31585 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN5 | Operation Message | Input Register | 0x04 | 30149 | 30150 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN6 | Operation Message | Input Register | 0x04 | 30184 | 30185 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN7 | Operation Message | Input Register | 0x04 | 30219 | 30220 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN8 | Operation Message | Input Register | 0x04 | 30254 | 30255 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_UpperRegLimit_VAL | Yes | Current MW upper regulation limit in controller for GEN9 | Operation Message | Input Register | 0x04 | 30289 | 30290 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Blackstart Sequence | N/A | N/A | CurrentStepFailed_VAL | Yes | Current step of blackstart sequence has failed, 2=step failed and continue button is not available to operator, 3=step failed and continue button is available to operator | Failure Message | Input Register | 0x04 | 2970 | 2970 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-1 GEN1 | Command | Coil | 0x05 | 0 | 0 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-1 GEN2 | Command | Coil | 0x05 | 8 | 8 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-1 GEN3 | Command | Coil | 0x05 | 16 | 16 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-1 GEN4 | Command | Coil | 0x05 | 24 | 24 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-10 GEN37 | Command | Coil | 0x05 | 288 | 288 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-10 GEN38 | Command | Coil | 0x05 | 296 | 296 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-10 GEN39 | Command | Coil | 0x05 | 304 | 304 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-10 GEN40 | Command | Coil | 0x05 | 312 | 312 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-11 GEN41 | Command | Coil | 0x05 | 320 | 320 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-11 GEN42 | Command | Coil | 0x05 | 328 | 328 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-11 GEN43 | Command | Coil | 0x05 | 336 | 336 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-11 GEN44 | Command | Coil | 0x05 | 344 | 344 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-12 GEN45 | Command | Coil | 0x05 | 352 | 352 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-12 GEN46 | Command | Coil | 0x05 | 360 | 360 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-2 GEN5 | Command | Coil | 0x05 | 32 | 32 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-2 GEN6 | Command | Coil | 0x05 | 40 | 40 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-2 GEN7 | Command | Coil | 0x05 | 48 | 48 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-2 GEN8 | Command | Coil | 0x05 | 56 | 56 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-3 GEN10 | Command | Coil | 0x05 | 72 | 72 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-3 GEN11 | Command | Coil | 0x05 | 80 | 80 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-3 GEN12 | Command | Coil | 0x05 | 88 | 88 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-3 GEN9 | Command | Coil | 0x05 | 64 | 64 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-4 GEN13 | Command | Coil | 0x05 | 96 | 96 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-4 GEN14 | Command | Coil | 0x05 | 104 | 104 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-4 GEN15 | Command | Coil | 0x05 | 112 | 112 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-4 GEN16 | Command | Coil | 0x05 | 120 | 120 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-5 GEN17 | Command | Coil | 0x05 | 128 | 128 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-5 GEN18 | Command | Coil | 0x05 | 136 | 136 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-5 GEN19 | Command | Coil | 0x05 | 144 | 144 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-5 GEN20 | Command | Coil | 0x05 | 152 | 152 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-6 GEN21 | Command | Coil | 0x05 | 160 | 160 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-6 GEN22 | Command | Coil | 0x05 | 168 | 168 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-6 GEN23 | Command | Coil | 0x05 | 176 | 176 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-6 GEN24 | Command | Coil | 0x05 | 184 | 184 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-7 GEN25 | Command | Coil | 0x05 | 192 | 192 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-7 GEN26 | Command | Coil | 0x05 | 200 | 200 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-7 GEN27 | Command | Coil | 0x05 | 208 | 208 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-7 GEN28 | Command | Coil | 0x05 | 216 | 216 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-8 GEN29 | Command | Coil | 0x05 | 224 | 224 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-8 GEN30 | Command | Coil | 0x05 | 232 | 232 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-8 GEN31 | Command | Coil | 0x05 | 240 | 240 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-8 GEN32 | Command | Coil | 0x05 | 248 | 248 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-9 GEN33 | Command | Coil | 0x05 | 256 | 256 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-9 GEN34 | Command | Coil | 0x05 | 264 | 264 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-9 GEN35 | Command | Coil | 0x05 | 272 | 272 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_Enable_CMD | Yes | Enable PowerMAX AGC for QPAC-9 GEN36 | Command | Coil | 0x05 | 280 | 280 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-1 GEN1 | Command | Coil | 0x05 | 6 | 6 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-1 GEN2 | Command | Coil | 0x05 | 14 | 14 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-1 GEN3 | Command | Coil | 0x05 | 22 | 22 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-1 GEN4 | Command | Coil | 0x05 | 30 | 30 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-10 GEN37 | Command | Coil | 0x05 | 294 | 294 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-10 GEN38 | Command | Coil | 0x05 | 302 | 302 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-10 GEN39 | Command | Coil | 0x05 | 310 | 310 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-10 GEN40 | Command | Coil | 0x05 | 318 | 318 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-11 GEN41 | Command | Coil | 0x05 | 326 | 326 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-11 GEN42 | Command | Coil | 0x05 | 334 | 334 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-11 GEN43 | Command | Coil | 0x05 | 342 | 342 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-11 GEN44 | Command | Coil | 0x05 | 350 | 350 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-12 GEN45 | Command | Coil | 0x05 | 358 | 358 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-12 GEN46 | Command | Coil | 0x05 | 366 | 366 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-2 GEN5 | Command | Coil | 0x05 | 38 | 38 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-2 GEN6 | Command | Coil | 0x05 | 46 | 46 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-2 GEN7 | Command | Coil | 0x05 | 54 | 54 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-2 GEN8 | Command | Coil | 0x05 | 62 | 62 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-3 GEN10 | Command | Coil | 0x05 | 78 | 78 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-3 GEN11 | Command | Coil | 0x05 | 86 | 86 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-3 GEN12 | Command | Coil | 0x05 | 94 | 94 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-3 GEN9 | Command | Coil | 0x05 | 70 | 70 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-4 GEN13 | Command | Coil | 0x05 | 102 | 102 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-4 GEN14 | Command | Coil | 0x05 | 110 | 110 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-4 GEN15 | Command | Coil | 0x05 | 118 | 118 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-4 GEN16 | Command | Coil | 0x05 | 126 | 126 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-5 GEN17 | Command | Coil | 0x05 | 134 | 134 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-5 GEN18 | Command | Coil | 0x05 | 142 | 142 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-5 GEN19 | Command | Coil | 0x05 | 150 | 150 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-5 GEN20 | Command | Coil | 0x05 | 158 | 158 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-6 GEN21 | Command | Coil | 0x05 | 166 | 166 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-6 GEN22 | Command | Coil | 0x05 | 174 | 174 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-6 GEN23 | Command | Coil | 0x05 | 182 | 182 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-6 GEN24 | Command | Coil | 0x05 | 190 | 190 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-7 GEN25 | Command | Coil | 0x05 | 198 | 198 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-7 GEN26 | Command | Coil | 0x05 | 206 | 206 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-7 GEN27 | Command | Coil | 0x05 | 214 | 214 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-7 GEN28 | Command | Coil | 0x05 | 222 | 222 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-8 GEN29 | Command | Coil | 0x05 | 230 | 230 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-8 GEN30 | Command | Coil | 0x05 | 238 | 238 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-8 GEN31 | Command | Coil | 0x05 | 246 | 246 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-8 GEN32 | Command | Coil | 0x05 | 254 | 254 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-9 GEN33 | Command | Coil | 0x05 | 262 | 262 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-9 GEN34 | Command | Coil | 0x05 | 270 | 270 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-9 GEN35 | Command | Coil | 0x05 | 278 | 278 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_Enable_CMD | Yes | Enable PowerMAX VCS for QPAC-9 GEN36 | Command | Coil | 0x05 | 286 | 286 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Generation Management Control Screens | N/A | N/A | GMS_MLMEnable_STAT | Yes | Enabled status for minimum load management | Operation Message | Discrete Input | 0x02 | 11201 | 11201 | 1 | Boolean | No | N/A | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN1 | Operation Message | Discrete Input | 0x02 | 10002 | 10002 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN1 | Operation Message | Discrete Input | 0x02 | 10013 | 10013 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN10 | Operation Message | Discrete Input | 0x02 | 10191 | 10191 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN10 | Operation Message | Discrete Input | 0x02 | 10202 | 10202 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN11 | Operation Message | Discrete Input | 0x02 | 10212 | 10212 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN11 | Operation Message | Discrete Input | 0x02 | 10223 | 10223 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN12 | Operation Message | Discrete Input | 0x02 | 10233 | 10233 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN12 | Operation Message | Discrete Input | 0x02 | 10244 | 10244 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN13 | Operation Message | Discrete Input | 0x02 | 10254 | 10254 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN13 | Operation Message | Discrete Input | 0x02 | 10265 | 10265 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN14 | Operation Message | Discrete Input | 0x02 | 10275 | 10275 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN14 | Operation Message | Discrete Input | 0x02 | 10286 | 10286 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN15 | Operation Message | Discrete Input | 0x02 | 10296 | 10296 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN15 | Operation Message | Discrete Input | 0x02 | 10307 | 10307 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN16 | Operation Message | Discrete Input | 0x02 | 10317 | 10317 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN16 | Operation Message | Discrete Input | 0x02 | 10328 | 10328 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN17 | Operation Message | Discrete Input | 0x02 | 10338 | 10338 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN17 | Operation Message | Discrete Input | 0x02 | 10349 | 10349 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN18 | Operation Message | Discrete Input | 0x02 | 10359 | 10359 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN18 | Operation Message | Discrete Input | 0x02 | 10370 | 10370 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN19 | Operation Message | Discrete Input | 0x02 | 10380 | 10380 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN19 | Operation Message | Discrete Input | 0x02 | 10391 | 10391 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN2 | Operation Message | Discrete Input | 0x02 | 10023 | 10023 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN2 | Operation Message | Discrete Input | 0x02 | 10034 | 10034 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN20 | Operation Message | Discrete Input | 0x02 | 10401 | 10401 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN20 | Operation Message | Discrete Input | 0x02 | 10412 | 10412 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN21 | Operation Message | Discrete Input | 0x02 | 10422 | 10422 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN21 | Operation Message | Discrete Input | 0x02 | 10433 | 10433 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN22 | Operation Message | Discrete Input | 0x02 | 10443 | 10443 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN22 | Operation Message | Discrete Input | 0x02 | 10454 | 10454 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN23 | Operation Message | Discrete Input | 0x02 | 10464 | 10464 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN23 | Operation Message | Discrete Input | 0x02 | 10475 | 10475 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN24 | Operation Message | Discrete Input | 0x02 | 10485 | 10485 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN24 | Operation Message | Discrete Input | 0x02 | 10496 | 10496 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN25 | Operation Message | Discrete Input | 0x02 | 10506 | 10506 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN25 | Operation Message | Discrete Input | 0x02 | 10517 | 10517 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN26 | Operation Message | Discrete Input | 0x02 | 10527 | 10527 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN26 | Operation Message | Discrete Input | 0x02 | 10538 | 10538 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN27 | Operation Message | Discrete Input | 0x02 | 10548 | 10548 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN27 | Operation Message | Discrete Input | 0x02 | 10559 | 10559 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN28 | Operation Message | Discrete Input | 0x02 | 10569 | 10569 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN28 | Operation Message | Discrete Input | 0x02 | 10580 | 10580 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN29 | Operation Message | Discrete Input | 0x02 | 10590 | 10590 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN29 | Operation Message | Discrete Input | 0x02 | 10601 | 10601 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN3 | Operation Message | Discrete Input | 0x02 | 10044 | 10044 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN3 | Operation Message | Discrete Input | 0x02 | 10055 | 10055 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN30 | Operation Message | Discrete Input | 0x02 | 10611 | 10611 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN30 | Operation Message | Discrete Input | 0x02 | 10622 | 10622 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN31 | Operation Message | Discrete Input | 0x02 | 10632 | 10632 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN31 | Operation Message | Discrete Input | 0x02 | 10643 | 10643 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN32 | Operation Message | Discrete Input | 0x02 | 10653 | 10653 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN32 | Operation Message | Discrete Input | 0x02 | 10664 | 10664 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN33 | Operation Message | Discrete Input | 0x02 | 10674 | 10674 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN33 | Operation Message | Discrete Input | 0x02 | 10685 | 10685 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN34 | Operation Message | Discrete Input | 0x02 | 10695 | 10695 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN34 | Operation Message | Discrete Input | 0x02 | 10706 | 10706 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN35 | Operation Message | Discrete Input | 0x02 | 10716 | 10716 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN35 | Operation Message | Discrete Input | 0x02 | 10727 | 10727 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN36 | Operation Message | Discrete Input | 0x02 | 10737 | 10737 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN36 | Operation Message | Discrete Input | 0x02 | 10748 | 10748 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN37 | Operation Message | Discrete Input | 0x02 | 10758 | 10758 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN37 | Operation Message | Discrete Input | 0x02 | 10769 | 10769 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN38 | Operation Message | Discrete Input | 0x02 | 10779 | 10779 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN38 | Operation Message | Discrete Input | 0x02 | 10790 | 10790 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN39 | Operation Message | Discrete Input | 0x02 | 10800 | 10800 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN39 | Operation Message | Discrete Input | 0x02 | 10811 | 10811 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN4 | Operation Message | Discrete Input | 0x02 | 10065 | 10065 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN4 | Operation Message | Discrete Input | 0x02 | 10076 | 10076 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN40 | Operation Message | Discrete Input | 0x02 | 10821 | 10821 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN40 | Operation Message | Discrete Input | 0x02 | 10832 | 10832 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN41 | Operation Message | Discrete Input | 0x02 | 10842 | 10842 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN41 | Operation Message | Discrete Input | 0x02 | 10853 | 10853 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN42 | Operation Message | Discrete Input | 0x02 | 10863 | 10863 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN42 | Operation Message | Discrete Input | 0x02 | 10874 | 10874 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN43 | Operation Message | Discrete Input | 0x02 | 10884 | 10884 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN43 | Operation Message | Discrete Input | 0x02 | 10895 | 10895 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN44 | Operation Message | Discrete Input | 0x02 | 10905 | 10905 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN44 | Operation Message | Discrete Input | 0x02 | 10916 | 10916 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN45 | Operation Message | Discrete Input | 0x02 | 10926 | 10926 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN45 | Operation Message | Discrete Input | 0x02 | 10937 | 10937 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN46 | Operation Message | Discrete Input | 0x02 | 10947 | 10947 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN46 | Operation Message | Discrete Input | 0x02 | 10958 | 10958 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN5 | Operation Message | Discrete Input | 0x02 | 10086 | 10086 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN5 | Operation Message | Discrete Input | 0x02 | 10097 | 10097 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN6 | Operation Message | Discrete Input | 0x02 | 10107 | 10107 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN6 | Operation Message | Discrete Input | 0x02 | 10118 | 10118 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN7 | Operation Message | Discrete Input | 0x02 | 10128 | 10128 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN7 | Operation Message | Discrete Input | 0x02 | 10139 | 10139 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN8 | Operation Message | Discrete Input | 0x02 | 10149 | 10149 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN8 | Operation Message | Discrete Input | 0x02 | 10160 | 10160 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN9 | Operation Message | Discrete Input | 0x02 | 10170 | 10170 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_Remote_STAT | Yes | Engine Ready for Automatic Demand - GEN9 | Operation Message | Discrete Input | 0x02 | 10181 | 10181 | 1 | Boolean | No | N/A | Latch | 0=local, 1=remote
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10011 | 10011 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10032 | 10032 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10053 | 10053 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10074 | 10074 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10095 | 10095 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10116 | 10116 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10137 | 10137 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10158 | 10158 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10179 | 10179 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10200 | 10200 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10221 | 10221 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10242 | 10242 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10263 | 10263 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10284 | 10284 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10305 | 10305 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10326 | 10326 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10347 | 10347 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10368 | 10368 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10389 | 10389 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10410 | 10410 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10431 | 10431 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10452 | 10452 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10473 | 10473 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10494 | 10494 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10515 | 10515 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10536 | 10536 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10557 | 10557 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10578 | 10578 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10599 | 10599 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10620 | 10620 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10641 | 10641 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10662 | 10662 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10683 | 10683 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10704 | 10704 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10725 | 10725 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10746 | 10746 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10767 | 10767 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10788 | 10788 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10809 | 10809 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10830 | 10830 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10851 | 10851 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10872 | 10872 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10893 | 10893 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10914 | 10914 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10935 | 10935 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_EngineTrip_STAT | Yes | Engine Trip Status from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10956 | 10956 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=trip
Network Overview Screen | N/A | N/A | FEP_Q1A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10973 | 10973 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q2A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10974 | 10974 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q3A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10975 | 10975 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q4A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10976 | 10976 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q5A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10977 | 10977 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q6A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10978 | 10978 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q7A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10979 | 10979 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q8A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10980 | 10980 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q9A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10981 | 10981 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q10A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10982 | 10982 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q11A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10983 | 10983 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q12A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10984 | 10984 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q1B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11009 | 11009 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q2B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11010 | 11010 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q3B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11011 | 11011 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q4B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11012 | 11012 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q5B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11013 | 11013 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q6B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11014 | 11014 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q7B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11015 | 11015 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q8B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11016 | 11016 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q9B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11017 | 11017 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q10B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11018 | 11018 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q11B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11019 | 11019 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q12B_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11020 | 11020 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_RTDS_Q1A_NGVL_HSAlarm_STAT | Yes | FEP high speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11045 | 11045 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q1A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10985 | 10985 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q2A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10986 | 10986 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q3A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10987 | 10987 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q4A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10988 | 10988 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q5A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10989 | 10989 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q6A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10990 | 10990 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q7A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10991 | 10991 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q8A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10992 | 10992 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q9A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10993 | 10993 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q10A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10994 | 10994 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q11A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10995 | 10995 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q12A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 10996 | 10996 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q1B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11021 | 11021 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q2B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11022 | 11022 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q3B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11023 | 11023 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q4B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11024 | 11024 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q5B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11025 | 11025 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q6B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11026 | 11026 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q7B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11027 | 11027 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q8B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11028 | 11028 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q9B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11029 | 11029 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q10B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11030 | 11030 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q11B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11031 | 11031 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_Q12B_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11032 | 11032 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Network Overview Screen | N/A | N/A | FEP_RTDS_Q1A_NGVL_LSAlarm_STAT | Yes | FEP low speed NGVL communications alarm | Failure Message | Discrete Input | 0x02 | 11046 | 11046 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-1 | GEN1 | GMS_G1_StartFailed_STAT | Yes | G1 failed to start | Failure Message | Discrete Input | 0x02 | 10019 | 10019 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-3 | GEN10 | GMS_G10_StartFailed_STAT | Yes | G10 failed to start | Failure Message | Discrete Input | 0x02 | 10208 | 10208 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-3 | GEN11 | GMS_G11_StartFailed_STAT | Yes | G11 failed to start | Failure Message | Discrete Input | 0x02 | 10229 | 10229 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-3 | GEN12 | GMS_G12_StartFailed_STAT | Yes | G12 failed to start | Failure Message | Discrete Input | 0x02 | 10250 | 10250 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-4 | GEN13 | GMS_G13_StartFailed_STAT | Yes | G13 failed to start | Failure Message | Discrete Input | 0x02 | 10271 | 10271 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-4 | GEN14 | GMS_G14_StartFailed_STAT | Yes | G14 failed to start | Failure Message | Discrete Input | 0x02 | 10292 | 10292 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-4 | GEN15 | GMS_G15_StartFailed_STAT | Yes | G15 failed to start | Failure Message | Discrete Input | 0x02 | 10313 | 10313 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-4 | GEN16 | GMS_G16_StartFailed_STAT | Yes | G16 failed to start | Failure Message | Discrete Input | 0x02 | 10334 | 10334 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-5 | GEN17 | GMS_G17_StartFailed_STAT | Yes | G17 failed to start | Failure Message | Discrete Input | 0x02 | 10355 | 10355 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-5 | GEN18 | GMS_G18_StartFailed_STAT | Yes | G18 failed to start | Failure Message | Discrete Input | 0x02 | 10376 | 10376 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-5 | GEN19 | GMS_G19_StartFailed_STAT | Yes | G19 failed to start | Failure Message | Discrete Input | 0x02 | 10397 | 10397 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-1 | G2 | GMS_G2_StartFailed_STAT | Yes | G2 failed to start | Failure Message | Discrete Input | 0x02 | 10040 | 10040 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-5 | G20 | GMS_G20_StartFailed_STAT | Yes | G20 failed to start | Failure Message | Discrete Input | 0x02 | 10418 | 10418 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-6 | G21 | GMS_G21_StartFailed_STAT | Yes | G21 failed to start | Failure Message | Discrete Input | 0x02 | 10439 | 10439 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-6 | G22 | GMS_G22_StartFailed_STAT | Yes | G22 failed to start | Failure Message | Discrete Input | 0x02 | 10460 | 10460 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-6 | G23 | GMS_G23_StartFailed_STAT | Yes | G23 failed to start | Failure Message | Discrete Input | 0x02 | 10481 | 10481 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-6 | G24 | GMS_G24_StartFailed_STAT | Yes | G24 failed to start | Failure Message | Discrete Input | 0x02 | 10502 | 10502 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-7 | G25 | GMS_G25_StartFailed_STAT | Yes | G25 failed to start | Failure Message | Discrete Input | 0x02 | 10523 | 10523 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-7 | G26 | GMS_G26_StartFailed_STAT | Yes | G26 failed to start | Failure Message | Discrete Input | 0x02 | 10544 | 10544 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-7 | G27 | GMS_G27_StartFailed_STAT | Yes | G27 failed to start | Failure Message | Discrete Input | 0x02 | 10565 | 10565 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-7 | G28 | GMS_G28_StartFailed_STAT | Yes | G28 failed to start | Failure Message | Discrete Input | 0x02 | 10586 | 10586 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-8 | G29 | GMS_G29_StartFailed_STAT | Yes | G29 failed to start | Failure Message | Discrete Input | 0x02 | 10607 | 10607 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-1 | G3 | GMS_G3_StartFailed_STAT | Yes | G3 failed to start | Failure Message | Discrete Input | 0x02 | 10061 | 10061 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-8 | G30 | GMS_G30_StartFailed_STAT | Yes | G30 failed to start | Failure Message | Discrete Input | 0x02 | 10628 | 10628 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-8 | G31 | GMS_G31_StartFailed_STAT | Yes | G31 failed to start | Failure Message | Discrete Input | 0x02 | 10649 | 10649 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-8 | G32 | GMS_G32_StartFailed_STAT | Yes | G32 failed to start | Failure Message | Discrete Input | 0x02 | 10670 | 10670 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-9 | G33 | GMS_G33_StartFailed_STAT | Yes | G33 failed to start | Failure Message | Discrete Input | 0x02 | 10691 | 10691 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-9 | G34 | GMS_G34_StartFailed_STAT | Yes | G34 failed to start | Failure Message | Discrete Input | 0x02 | 10712 | 10712 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-9 | G35 | GMS_G35_StartFailed_STAT | Yes | G35 failed to start | Failure Message | Discrete Input | 0x02 | 10733 | 10733 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-9 | G36 | GMS_G36_StartFailed_STAT | Yes | G36 failed to start | Failure Message | Discrete Input | 0x02 | 10754 | 10754 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-10 | G37 | GMS_G37_StartFailed_STAT | Yes | G37 failed to start | Failure Message | Discrete Input | 0x02 | 10775 | 10775 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-10 | G38 | GMS_G38_StartFailed_STAT | Yes | G38 failed to start | Failure Message | Discrete Input | 0x02 | 10796 | 10796 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-10 | G39 | GMS_G39_StartFailed_STAT | Yes | G39 failed to start | Failure Message | Discrete Input | 0x02 | 10817 | 10817 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-1 | G4 | GMS_G4_StartFailed_STAT | Yes | G4 failed to start | Failure Message | Discrete Input | 0x02 | 10082 | 10082 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-10 | G40 | GMS_G40_StartFailed_STAT | Yes | G40 failed to start | Failure Message | Discrete Input | 0x02 | 10838 | 10838 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-11 | G41 | GMS_G41_StartFailed_STAT | Yes | G41 failed to start | Failure Message | Discrete Input | 0x02 | 10859 | 10859 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-11 | G42 | GMS_G42_StartFailed_STAT | Yes | G42 failed to start | Failure Message | Discrete Input | 0x02 | 10880 | 10880 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-11 | G43 | GMS_G43_StartFailed_STAT | Yes | G43 failed to start | Failure Message | Discrete Input | 0x02 | 10901 | 10901 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-11 | G44 | GMS_G44_StartFailed_STAT | Yes | G44 failed to start | Failure Message | Discrete Input | 0x02 | 10922 | 10922 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-12 | G45 | GMS_G45_StartFailed_STAT | Yes | G45 failed to start | Failure Message | Discrete Input | 0x02 | 10943 | 10943 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-12 | G46 | GMS_G46_StartFailed_STAT | Yes | G46 failed to start | Failure Message | Discrete Input | 0x02 | 10964 | 10964 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-2 | G5 | GMS_G5_StartFailed_STAT | Yes | G5 failed to start | Failure Message | Discrete Input | 0x02 | 10103 | 10103 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-2 | G6 | GMS_G6_StartFailed_STAT | Yes | G6 failed to start | Failure Message | Discrete Input | 0x02 | 10124 | 10124 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-2 | G7 | GMS_G7_StartFailed_STAT | Yes | G7 failed to start | Failure Message | Discrete Input | 0x02 | 10145 | 10145 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-2 | G8 | GMS_G8_StartFailed_STAT | Yes | G8 failed to start | Failure Message | Discrete Input | 0x02 | 10166 | 10166 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-3 | G9 | GMS_G9_StartFailed_STAT | Yes | G9 failed to start | Failure Message | Discrete Input | 0x02 | 10187 | 10187 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | N/A | N/A | GCS_Enabled_STAT | Yes | GCS control enabled status |  | Discrete Input | 0x02 | 11049 | 11049 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_BreakerOpFailure_STAT | Yes | GEN1 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10009 | 10009 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_DelayedShutdown_STAT | Yes | GEN1 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10010 | 10010 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-1 | GEN1 | GMS_G1_StopFailed_STAT | Yes | GEN1 failed to stop | Alarm Message | Discrete Input | 0x02 | 10020 | 10020 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_EngineDemanded_STAT | Yes | GEN1 is demanded status | Operation Message | Discrete Input | 0x02 | 10008 | 10008 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_BreakerOpFailure_STAT | Yes | GEN10 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10198 | 10198 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_DelayedShutdown_STAT | Yes | GEN10 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10199 | 10199 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-3 | GEN10 | GMS_G10_StopFailed_STAT | Yes | GEN10 failed to stop | Alarm Message | Discrete Input | 0x02 | 10209 | 10209 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_EngineDemanded_STAT | Yes | GEN10 is demanded status | Operation Message | Discrete Input | 0x02 | 10197 | 10197 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_BreakerOpFailure_STAT | Yes | GEN11 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10219 | 10219 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_DelayedShutdown_STAT | Yes | GEN11 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10220 | 10220 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-3 | GEN11 | GMS_G11_StopFailed_STAT | Yes | GEN11 failed to stop | Alarm Message | Discrete Input | 0x02 | 10230 | 10230 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_EngineDemanded_STAT | Yes | GEN11 is demanded status | Operation Message | Discrete Input | 0x02 | 10218 | 10218 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_BreakerOpFailure_STAT | Yes | GEN12 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10240 | 10240 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_DelayedShutdown_STAT | Yes | GEN12 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10241 | 10241 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-3 | GEN12 | GMS_G12_StopFailed_STAT | Yes | GEN12 failed to stop | Alarm Message | Discrete Input | 0x02 | 10251 | 10251 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_EngineDemanded_STAT | Yes | GEN12 is demanded status | Operation Message | Discrete Input | 0x02 | 10239 | 10239 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_BreakerOpFailure_STAT | Yes | GEN13 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10261 | 10261 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_DelayedShutdown_STAT | Yes | GEN13 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10262 | 10262 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-4 | GEN13 | GMS_G13_StopFailed_STAT | Yes | GEN13 failed to stop | Alarm Message | Discrete Input | 0x02 | 10272 | 10272 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_EngineDemanded_STAT | Yes | GEN13 is demanded status | Operation Message | Discrete Input | 0x02 | 10260 | 10260 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_BreakerOpFailure_STAT | Yes | GEN14 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10282 | 10282 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_DelayedShutdown_STAT | Yes | GEN14 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10283 | 10283 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-4 | GEN14 | GMS_G14_StopFailed_STAT | Yes | GEN14 failed to stop | Alarm Message | Discrete Input | 0x02 | 10293 | 10293 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_EngineDemanded_STAT | Yes | GEN14 is demanded status | Operation Message | Discrete Input | 0x02 | 10281 | 10281 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_BreakerOpFailure_STAT | Yes | GEN15 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10303 | 10303 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_DelayedShutdown_STAT | Yes | GEN15 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10304 | 10304 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-4 | GEN15 | GMS_G15_StopFailed_STAT | Yes | GEN15 failed to stop | Alarm Message | Discrete Input | 0x02 | 10314 | 10314 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_EngineDemanded_STAT | Yes | GEN15 is demanded status | Operation Message | Discrete Input | 0x02 | 10302 | 10302 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_BreakerOpFailure_STAT | Yes | GEN16 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10324 | 10324 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_DelayedShutdown_STAT | Yes | GEN16 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10325 | 10325 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-4 | GEN16 | GMS_G16_StopFailed_STAT | Yes | GEN16 failed to stop | Alarm Message | Discrete Input | 0x02 | 10335 | 10335 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_EngineDemanded_STAT | Yes | GEN16 is demanded status | Operation Message | Discrete Input | 0x02 | 10323 | 10323 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_BreakerOpFailure_STAT | Yes | GEN17 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10345 | 10345 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_DelayedShutdown_STAT | Yes | GEN17 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10346 | 10346 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-5 | GEN17 | GMS_G17_StopFailed_STAT | Yes | GEN17 failed to stop | Alarm Message | Discrete Input | 0x02 | 10356 | 10356 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_EngineDemanded_STAT | Yes | GEN17 is demanded status | Operation Message | Discrete Input | 0x02 | 10344 | 10344 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_BreakerOpFailure_STAT | Yes | GEN18 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10366 | 10366 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_DelayedShutdown_STAT | Yes | GEN18 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10367 | 10367 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-5 | GEN18 | GMS_G18_StopFailed_STAT | Yes | GEN18 failed to stop | Alarm Message | Discrete Input | 0x02 | 10377 | 10377 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_EngineDemanded_STAT | Yes | GEN18 is demanded status | Operation Message | Discrete Input | 0x02 | 10365 | 10365 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_BreakerOpFailure_STAT | Yes | GEN19 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10387 | 10387 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_DelayedShutdown_STAT | Yes | GEN19 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10388 | 10388 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-5 | GEN19 | GMS_G19_StopFailed_STAT | Yes | GEN19 failed to stop | Alarm Message | Discrete Input | 0x02 | 10398 | 10398 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_EngineDemanded_STAT | Yes | GEN19 is demanded status | Operation Message | Discrete Input | 0x02 | 10386 | 10386 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_BreakerOpFailure_STAT | Yes | GEN2 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10030 | 10030 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_DelayedShutdown_STAT | Yes | GEN2 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10031 | 10031 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-1 | GEN2 | GMS_G2_StopFailed_STAT | Yes | GEN2 failed to stop | Alarm Message | Discrete Input | 0x02 | 10041 | 10041 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_EngineDemanded_STAT | Yes | GEN2 is demanded status | Operation Message | Discrete Input | 0x02 | 10029 | 10029 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_BreakerOpFailure_STAT | Yes | GEN20 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10408 | 10408 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_DelayedShutdown_STAT | Yes | GEN20 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10409 | 10409 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-5 | GEN20 | GMS_G20_StopFailed_STAT | Yes | GEN20 failed to stop | Alarm Message | Discrete Input | 0x02 | 10419 | 10419 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_EngineDemanded_STAT | Yes | GEN20 is demanded status | Operation Message | Discrete Input | 0x02 | 10407 | 10407 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_BreakerOpFailure_STAT | Yes | GEN21 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10429 | 10429 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_DelayedShutdown_STAT | Yes | GEN21 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10430 | 10430 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-6 | GEN21 | GMS_G21_StopFailed_STAT | Yes | GEN21 failed to stop | Alarm Message | Discrete Input | 0x02 | 10440 | 10440 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_EngineDemanded_STAT | Yes | GEN21 is demanded status | Operation Message | Discrete Input | 0x02 | 10428 | 10428 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_BreakerOpFailure_STAT | Yes | GEN22 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10450 | 10450 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_DelayedShutdown_STAT | Yes | GEN22 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10451 | 10451 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-6 | GEN22 | GMS_G22_StopFailed_STAT | Yes | GEN22 failed to stop | Alarm Message | Discrete Input | 0x02 | 10461 | 10461 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_EngineDemanded_STAT | Yes | GEN22 is demanded status | Operation Message | Discrete Input | 0x02 | 10449 | 10449 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_BreakerOpFailure_STAT | Yes | GEN23 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10471 | 10471 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_DelayedShutdown_STAT | Yes | GEN23 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10472 | 10472 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-6 | GEN23 | GMS_G23_StopFailed_STAT | Yes | GEN23 failed to stop | Alarm Message | Discrete Input | 0x02 | 10482 | 10482 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_EngineDemanded_STAT | Yes | GEN23 is demanded status | Operation Message | Discrete Input | 0x02 | 10470 | 10470 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_BreakerOpFailure_STAT | Yes | GEN24 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10492 | 10492 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_DelayedShutdown_STAT | Yes | GEN24 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10493 | 10493 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-6 | GEN24 | GMS_G24_StopFailed_STAT | Yes | GEN24 failed to stop | Alarm Message | Discrete Input | 0x02 | 10503 | 10503 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_EngineDemanded_STAT | Yes | GEN24 is demanded status | Operation Message | Discrete Input | 0x02 | 10491 | 10491 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_BreakerOpFailure_STAT | Yes | GEN25 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10513 | 10513 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_DelayedShutdown_STAT | Yes | GEN25 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10514 | 10514 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-7 | GEN25 | GMS_G25_StopFailed_STAT | Yes | GEN25 failed to stop | Alarm Message | Discrete Input | 0x02 | 10524 | 10524 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_EngineDemanded_STAT | Yes | GEN25 is demanded status | Operation Message | Discrete Input | 0x02 | 10512 | 10512 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_BreakerOpFailure_STAT | Yes | GEN26 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10534 | 10534 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_DelayedShutdown_STAT | Yes | GEN26 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10535 | 10535 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-7 | GEN26 | GMS_G26_StopFailed_STAT | Yes | GEN26 failed to stop | Alarm Message | Discrete Input | 0x02 | 10545 | 10545 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_EngineDemanded_STAT | Yes | GEN26 is demanded status | Operation Message | Discrete Input | 0x02 | 10533 | 10533 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_BreakerOpFailure_STAT | Yes | GEN27 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10555 | 10555 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_DelayedShutdown_STAT | Yes | GEN27 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10556 | 10556 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-7 | GEN27 | GMS_G27_StopFailed_STAT | Yes | GEN27 failed to stop | Alarm Message | Discrete Input | 0x02 | 10566 | 10566 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_EngineDemanded_STAT | Yes | GEN27 is demanded status | Operation Message | Discrete Input | 0x02 | 10554 | 10554 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_BreakerOpFailure_STAT | Yes | GEN28 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10576 | 10576 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_DelayedShutdown_STAT | Yes | GEN28 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10577 | 10577 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-7 | GEN28 | GMS_G28_StopFailed_STAT | Yes | GEN28 failed to stop | Alarm Message | Discrete Input | 0x02 | 10587 | 10587 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_EngineDemanded_STAT | Yes | GEN28 is demanded status | Operation Message | Discrete Input | 0x02 | 10575 | 10575 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_BreakerOpFailure_STAT | Yes | GEN29 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10597 | 10597 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_DelayedShutdown_STAT | Yes | GEN29 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10598 | 10598 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-8 | GEN29 | GMS_G29_StopFailed_STAT | Yes | GEN29 failed to stop | Alarm Message | Discrete Input | 0x02 | 10608 | 10608 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_EngineDemanded_STAT | Yes | GEN29 is demanded status | Operation Message | Discrete Input | 0x02 | 10596 | 10596 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_BreakerOpFailure_STAT | Yes | GEN3 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10051 | 10051 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_DelayedShutdown_STAT | Yes | GEN3 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10052 | 10052 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-1 | GEN3 | GMS_G3_StopFailed_STAT | Yes | GEN3 failed to stop | Alarm Message | Discrete Input | 0x02 | 10062 | 10062 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_EngineDemanded_STAT | Yes | GEN3 is demanded status | Operation Message | Discrete Input | 0x02 | 10050 | 10050 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_BreakerOpFailure_STAT | Yes | GEN30 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10618 | 10618 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_DelayedShutdown_STAT | Yes | GEN30 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10619 | 10619 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-8 | GEN30 | GMS_G30_StopFailed_STAT | Yes | GEN30 failed to stop | Alarm Message | Discrete Input | 0x02 | 10629 | 10629 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_EngineDemanded_STAT | Yes | GEN30 is demanded status | Operation Message | Discrete Input | 0x02 | 10617 | 10617 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_BreakerOpFailure_STAT | Yes | GEN31 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10639 | 10639 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_DelayedShutdown_STAT | Yes | GEN31 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10640 | 10640 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-8 | GEN31 | GMS_G31_StopFailed_STAT | Yes | GEN31 failed to stop | Alarm Message | Discrete Input | 0x02 | 10650 | 10650 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_EngineDemanded_STAT | Yes | GEN31 is demanded status | Operation Message | Discrete Input | 0x02 | 10638 | 10638 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_BreakerOpFailure_STAT | Yes | GEN32 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10660 | 10660 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_DelayedShutdown_STAT | Yes | GEN32 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10661 | 10661 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-8 | GEN32 | GMS_G32_StopFailed_STAT | Yes | GEN32 failed to stop | Alarm Message | Discrete Input | 0x02 | 10671 | 10671 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_EngineDemanded_STAT | Yes | GEN32 is demanded status | Operation Message | Discrete Input | 0x02 | 10659 | 10659 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_BreakerOpFailure_STAT | Yes | GEN33 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10681 | 10681 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_DelayedShutdown_STAT | Yes | GEN33 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10682 | 10682 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-9 | GEN33 | GMS_G33_StopFailed_STAT | Yes | GEN33 failed to stop | Alarm Message | Discrete Input | 0x02 | 10692 | 10692 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_EngineDemanded_STAT | Yes | GEN33 is demanded status | Operation Message | Discrete Input | 0x02 | 10680 | 10680 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_BreakerOpFailure_STAT | Yes | GEN34 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10702 | 10702 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_DelayedShutdown_STAT | Yes | GEN34 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10703 | 10703 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-9 | GEN34 | GMS_G34_StopFailed_STAT | Yes | GEN34 failed to stop | Alarm Message | Discrete Input | 0x02 | 10713 | 10713 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_EngineDemanded_STAT | Yes | GEN34 is demanded status | Operation Message | Discrete Input | 0x02 | 10701 | 10701 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_BreakerOpFailure_STAT | Yes | GEN35 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10723 | 10723 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_DelayedShutdown_STAT | Yes | GEN35 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10724 | 10724 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-9 | GEN35 | GMS_G35_StopFailed_STAT | Yes | GEN35 failed to stop | Alarm Message | Discrete Input | 0x02 | 10734 | 10734 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_EngineDemanded_STAT | Yes | GEN35 is demanded status | Operation Message | Discrete Input | 0x02 | 10722 | 10722 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_BreakerOpFailure_STAT | Yes | GEN36 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10744 | 10744 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_DelayedShutdown_STAT | Yes | GEN36 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10745 | 10745 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-9 | GEN36 | GMS_G36_StopFailed_STAT | Yes | GEN36 failed to stop | Alarm Message | Discrete Input | 0x02 | 10755 | 10755 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_EngineDemanded_STAT | Yes | GEN36 is demanded status | Operation Message | Discrete Input | 0x02 | 10743 | 10743 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_BreakerOpFailure_STAT | Yes | GEN37 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10765 | 10765 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_DelayedShutdown_STAT | Yes | GEN37 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10766 | 10766 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-10 | GEN37 | GMS_G37_StopFailed_STAT | Yes | GEN37 failed to stop | Alarm Message | Discrete Input | 0x02 | 10776 | 10776 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_EngineDemanded_STAT | Yes | GEN37 is demanded status | Operation Message | Discrete Input | 0x02 | 10764 | 10764 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_BreakerOpFailure_STAT | Yes | GEN38 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10786 | 10786 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_DelayedShutdown_STAT | Yes | GEN38 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10787 | 10787 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-10 | GEN38 | GMS_G38_StopFailed_STAT | Yes | GEN38 failed to stop | Alarm Message | Discrete Input | 0x02 | 10797 | 10797 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_EngineDemanded_STAT | Yes | GEN38 is demanded status | Operation Message | Discrete Input | 0x02 | 10785 | 10785 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_BreakerOpFailure_STAT | Yes | GEN39 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10807 | 10807 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_DelayedShutdown_STAT | Yes | GEN39 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10808 | 10808 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-10 | GEN39 | GMS_G39_StopFailed_STAT | Yes | GEN39 failed to stop | Alarm Message | Discrete Input | 0x02 | 10818 | 10818 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_EngineDemanded_STAT | Yes | GEN39 is demanded status | Operation Message | Discrete Input | 0x02 | 10806 | 10806 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_BreakerOpFailure_STAT | Yes | GEN4 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10072 | 10072 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_DelayedShutdown_STAT | Yes | GEN4 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10073 | 10073 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-1 | GEN4 | GMS_G4_StopFailed_STAT | Yes | GEN4 failed to stop | Alarm Message | Discrete Input | 0x02 | 10083 | 10083 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_EngineDemanded_STAT | Yes | GEN4 is demanded status | Operation Message | Discrete Input | 0x02 | 10071 | 10071 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_BreakerOpFailure_STAT | Yes | GEN40 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10828 | 10828 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_DelayedShutdown_STAT | Yes | GEN40 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10829 | 10829 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-10 | GEN40 | GMS_G40_StopFailed_STAT | Yes | GEN40 failed to stop | Alarm Message | Discrete Input | 0x02 | 10839 | 10839 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_EngineDemanded_STAT | Yes | GEN40 is demanded status | Operation Message | Discrete Input | 0x02 | 10827 | 10827 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_BreakerOpFailure_STAT | Yes | GEN41 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10849 | 10849 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_DelayedShutdown_STAT | Yes | GEN41 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10850 | 10850 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-11 | GEN41 | GMS_G41_StopFailed_STAT | Yes | GEN41 failed to stop | Alarm Message | Discrete Input | 0x02 | 10860 | 10860 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_EngineDemanded_STAT | Yes | GEN41 is demanded status | Operation Message | Discrete Input | 0x02 | 10848 | 10848 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_BreakerOpFailure_STAT | Yes | GEN42 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10870 | 10870 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_DelayedShutdown_STAT | Yes | GEN42 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10871 | 10871 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-11 | GEN42 | GMS_G42_StopFailed_STAT | Yes | GEN42 failed to stop | Alarm Message | Discrete Input | 0x02 | 10881 | 10881 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_EngineDemanded_STAT | Yes | GEN42 is demanded status | Operation Message | Discrete Input | 0x02 | 10869 | 10869 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_BreakerOpFailure_STAT | Yes | GEN43 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10891 | 10891 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_DelayedShutdown_STAT | Yes | GEN43 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10892 | 10892 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-11 | GEN43 | GMS_G43_StopFailed_STAT | Yes | GEN43 failed to stop | Alarm Message | Discrete Input | 0x02 | 10902 | 10902 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_EngineDemanded_STAT | Yes | GEN43 is demanded status | Operation Message | Discrete Input | 0x02 | 10890 | 10890 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_BreakerOpFailure_STAT | Yes | GEN44 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10912 | 10912 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_DelayedShutdown_STAT | Yes | GEN44 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10913 | 10913 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-11 | GEN44 | GMS_G44_StopFailed_STAT | Yes | GEN44 failed to stop | Alarm Message | Discrete Input | 0x02 | 10923 | 10923 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_EngineDemanded_STAT | Yes | GEN44 is demanded status | Operation Message | Discrete Input | 0x02 | 10911 | 10911 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_BreakerOpFailure_STAT | Yes | GEN45 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10933 | 10933 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_DelayedShutdown_STAT | Yes | GEN45 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10934 | 10934 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-12 | GEN45 | GMS_G45_StopFailed_STAT | Yes | GEN45 failed to stop | Alarm Message | Discrete Input | 0x02 | 10944 | 10944 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_EngineDemanded_STAT | Yes | GEN45 is demanded status | Operation Message | Discrete Input | 0x02 | 10932 | 10932 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_BreakerOpFailure_STAT | Yes | GEN46 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10954 | 10954 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_DelayedShutdown_STAT | Yes | GEN46 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10955 | 10955 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-12 | GEN46 | GMS_G46_StopFailed_STAT | Yes | GEN46 failed to stop | Alarm Message | Discrete Input | 0x02 | 10965 | 10965 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_EngineDemanded_STAT | Yes | GEN46 is demanded status | Operation Message | Discrete Input | 0x02 | 10953 | 10953 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_BreakerOpFailure_STAT | Yes | GEN5 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10093 | 10093 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_DelayedShutdown_STAT | Yes | GEN5 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10094 | 10094 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-2 | GEN5 | GMS_G5_StopFailed_STAT | Yes | GEN5 failed to stop | Alarm Message | Discrete Input | 0x02 | 10104 | 10104 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_EngineDemanded_STAT | Yes | GEN5 is demanded status | Operation Message | Discrete Input | 0x02 | 10092 | 10092 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_BreakerOpFailure_STAT | Yes | GEN6 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10114 | 10114 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_DelayedShutdown_STAT | Yes | GEN6 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10115 | 10115 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-2 | GEN6 | GMS_G6_StopFailed_STAT | Yes | GEN6 failed to stop | Alarm Message | Discrete Input | 0x02 | 10125 | 10125 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_EngineDemanded_STAT | Yes | GEN6 is demanded status | Operation Message | Discrete Input | 0x02 | 10113 | 10113 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_BreakerOpFailure_STAT | Yes | GEN7 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10135 | 10135 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_DelayedShutdown_STAT | Yes | GEN7 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10136 | 10136 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-2 | GEN7 | GMS_G7_StopFailed_STAT | Yes | GEN7 failed to stop | Alarm Message | Discrete Input | 0x02 | 10146 | 10146 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_EngineDemanded_STAT | Yes | GEN7 is demanded status | Operation Message | Discrete Input | 0x02 | 10134 | 10134 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_BreakerOpFailure_STAT | Yes | GEN8 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10156 | 10156 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_DelayedShutdown_STAT | Yes | GEN8 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10157 | 10157 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-2 | GEN8 | GMS_G8_StopFailed_STAT | Yes | GEN8 failed to stop | Alarm Message | Discrete Input | 0x02 | 10167 | 10167 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_EngineDemanded_STAT | Yes | GEN8 is demanded status | Operation Message | Discrete Input | 0x02 | 10155 | 10155 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_BreakerOpFailure_STAT | Yes | GEN9 700G Breaker Open Failure | Failure Message | Discrete Input | 0x02 | 10177 | 10177 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_DelayedShutdown_STAT | Yes | GEN9 delayed shutdown from DIA.NE | Alarm Message | Discrete Input | 0x02 | 10178 | 10178 | 1 | Boolean | No | N/A | Latch | 1 = Delayed Shutdown Active, 0 = Normal
Generation Management Control Screens | QPAC-3 | GEN9 | GMS_G9_StopFailed_STAT | Yes | GEN9 failed to stop | Alarm Message | Discrete Input | 0x02 | 10188 | 10188 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_EngineDemanded_STAT | Yes | GEN9 is demanded status | Operation Message | Discrete Input | 0x02 | 10176 | 10176 | 1 | Boolean | No | N/A | Latch | 0=not demanded, 1=engine demanded
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10004 | 10004 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10015 | 10015 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10025 | 10025 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10036 | 10036 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10046 | 10046 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10057 | 10057 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10067 | 10067 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10078 | 10078 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10088 | 10088 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10099 | 10099 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10109 | 10109 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10120 | 10120 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10130 | 10130 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10141 | 10141 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10151 | 10151 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10162 | 10162 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10172 | 10172 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10183 | 10183 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10193 | 10193 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10204 | 10204 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10214 | 10214 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10225 | 10225 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10235 | 10235 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10246 | 10246 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10256 | 10256 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10267 | 10267 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10277 | 10277 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10288 | 10288 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10298 | 10298 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10309 | 10309 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10319 | 10319 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10330 | 10330 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10340 | 10340 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10351 | 10351 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10361 | 10361 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10372 | 10372 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10382 | 10382 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10393 | 10393 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10403 | 10403 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10414 | 10414 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10424 | 10424 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10435 | 10435 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10445 | 10445 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10456 | 10456 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10466 | 10466 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10477 | 10477 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10487 | 10487 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10498 | 10498 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10508 | 10508 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10519 | 10519 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10529 | 10529 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10540 | 10540 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10550 | 10550 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10561 | 10561 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10571 | 10571 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10582 | 10582 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10592 | 10592 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10603 | 10603 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10613 | 10613 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10624 | 10624 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10634 | 10634 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10645 | 10645 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10655 | 10655 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10666 | 10666 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10676 | 10676 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10687 | 10687 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10697 | 10697 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10708 | 10708 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10718 | 10718 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10729 | 10729 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10739 | 10739 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10750 | 10750 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10760 | 10760 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10771 | 10771 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10781 | 10781 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10792 | 10792 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10802 | 10802 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10813 | 10813 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10823 | 10823 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10834 | 10834 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10844 | 10844 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10855 | 10855 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10865 | 10865 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10876 | 10876 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10886 | 10886 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10897 | 10897 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10907 | 10907 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10918 | 10918 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10928 | 10928 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10939 | 10939 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10949 | 10949 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_AtCapacity_STAT | Yes | Generator is operating at lower regulation or upper regulation limit set on the HMI | Alarm Message | Discrete Input | 0x02 | 10960 | 10960 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Generation Management Control Screens | QPAC-1 | GEN1 | GMS_G1_GensetOpMode_VAL | Yes | Generator operation mode for GEN1 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 2995 | 2995 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN10 | GMS_G10_GensetOpMode_VAL | Yes | Generator operation mode for GEN10 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3004 | 3004 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN11 | GMS_G11_GensetOpMode_VAL | Yes | Generator operation mode for GEN11 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3005 | 3005 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN12 | GMS_G12_GensetOpMode_VAL | Yes | Generator operation mode for GEN12 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3006 | 3006 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN13 | GMS_G13_GensetOpMode_VAL | Yes | Generator operation mode for GEN13 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3007 | 3007 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN14 | GMS_G14_GensetOpMode_VAL | Yes | Generator operation mode for GEN14 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3008 | 3008 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN15 | GMS_G15_GensetOpMode_VAL | Yes | Generator operation mode for GEN15 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3009 | 3009 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN16 | GMS_G16_GensetOpMode_VAL | Yes | Generator operation mode for GEN16 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3010 | 3010 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN17 | GMS_G17_GensetOpMode_VAL | Yes | Generator operation mode for GEN17 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3011 | 3011 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN18 | GMS_G18_GensetOpMode_VAL | Yes | Generator operation mode for GEN18 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3012 | 3012 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN19 | GMS_G19_GensetOpMode_VAL | Yes | Generator operation mode for GEN19 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3013 | 3013 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN2 | GMS_G2_GensetOpMode_VAL | Yes | Generator operation mode for GEN2 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 2996 | 2996 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN20 | GMS_G20_GensetOpMode_VAL | Yes | Generator operation mode for GEN20 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3014 | 3014 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN21 | GMS_G21_GensetOpMode_VAL | Yes | Generator operation mode for GEN21 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3015 | 3015 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN22 | GMS_G22_GensetOpMode_VAL | Yes | Generator operation mode for GEN22 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3016 | 3016 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN23 | GMS_G23_GensetOpMode_VAL | Yes | Generator operation mode for GEN23 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3017 | 3017 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN24 | GMS_G24_GensetOpMode_VAL | Yes | Generator operation mode for GEN24 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3018 | 3018 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN25 | GMS_G25_GensetOpMode_VAL | Yes | Generator operation mode for GEN25 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3019 | 3019 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN26 | GMS_G26_GensetOpMode_VAL | Yes | Generator operation mode for GEN26 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3020 | 3020 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN27 | GMS_G27_GensetOpMode_VAL | Yes | Generator operation mode for GEN27 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3021 | 3021 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN28 | GMS_G28_GensetOpMode_VAL | Yes | Generator operation mode for GEN28 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3022 | 3022 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN29 | GMS_G29_GensetOpMode_VAL | Yes | Generator operation mode for GEN29 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3023 | 3023 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN3 | GMS_G3_GensetOpMode_VAL | Yes | Generator operation mode for GEN3 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 2997 | 2997 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN30 | GMS_G30_GensetOpMode_VAL | Yes | Generator operation mode for GEN30 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3024 | 3024 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN31 | GMS_G31_GensetOpMode_VAL | Yes | Generator operation mode for GEN31 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3025 | 3025 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN32 | GMS_G32_GensetOpMode_VAL | Yes | Generator operation mode for GEN32 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3026 | 3026 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN33 | GMS_G33_GensetOpMode_VAL | Yes | Generator operation mode for GEN33 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3027 | 3027 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN34 | GMS_G34_GensetOpMode_VAL | Yes | Generator operation mode for GEN34 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3028 | 3028 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN35 | GMS_G35_GensetOpMode_VAL | Yes | Generator operation mode for GEN35 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3029 | 3029 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN36 | GMS_G36_GensetOpMode_VAL | Yes | Generator operation mode for GEN36 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3030 | 3030 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN37 | GMS_G37_GensetOpMode_VAL | Yes | Generator operation mode for GEN37 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3031 | 3031 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN38 | GMS_G38_GensetOpMode_VAL | Yes | Generator operation mode for GEN38 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3032 | 3032 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN39 | GMS_G39_GensetOpMode_VAL | Yes | Generator operation mode for GEN39 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3033 | 3033 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN4 | GMS_G4_GensetOpMode_VAL | Yes | Generator operation mode for GEN4 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 2998 | 2998 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN40 | GMS_G40_GensetOpMode_VAL | Yes | Generator operation mode for GEN40 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3034 | 3034 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN41 | GMS_G41_GensetOpMode_VAL | Yes | Generator operation mode for GEN41 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3035 | 3035 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN42 | GMS_G42_GensetOpMode_VAL | Yes | Generator operation mode for GEN42 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3036 | 3036 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN43 | GMS_G43_GensetOpMode_VAL | Yes | Generator operation mode for GEN43 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3037 | 3037 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN44 | GMS_G44_GensetOpMode_VAL | Yes | Generator operation mode for GEN44 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3038 | 3038 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-12 | GEN45 | GMS_G45_GensetOpMode_VAL | Yes | Generator operation mode for GEN45 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3039 | 3039 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-12 | GEN46 | GMS_G46_GensetOpMode_VAL | Yes | Generator operation mode for GEN46 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3040 | 3040 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN5 | GMS_G5_GensetOpMode_VAL | Yes | Generator operation mode for GEN5 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 2999 | 2999 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN6 | GMS_G6_GensetOpMode_VAL | Yes | Generator operation mode for GEN6 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3000 | 3000 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN7 | GMS_G7_GensetOpMode_VAL | Yes | Generator operation mode for GEN7 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3001 | 3001 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN8 | GMS_G8_GensetOpMode_VAL | Yes | Generator operation mode for GEN8 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3002 | 3002 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN9 | GMS_G9_GensetOpMode_VAL | Yes | Generator operation mode for GEN9 0=manual, 1=auto, 2=block |  | Input Register | 0x04 | 3003 | 3003 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_OpStatus_VAL | Yes | Generator running status for GEN1; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30032 | 30032 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_OpStatus_VAL | Yes | Generator running status for GEN10; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30347 | 30347 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_OpStatus_VAL | Yes | Generator running status for GEN11; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30382 | 30382 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_OpStatus_VAL | Yes | Generator running status for GEN12; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30417 | 30417 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_OpStatus_VAL | Yes | Generator running status for GEN13; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30452 | 30452 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_OpStatus_VAL | Yes | Generator running status for GEN14; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30487 | 30487 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_OpStatus_VAL | Yes | Generator running status for GEN15; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30522 | 30522 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_OpStatus_VAL | Yes | Generator running status for GEN16; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30557 | 30557 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_OpStatus_VAL | Yes | Generator running status for GEN17; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30592 | 30592 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_OpStatus_VAL | Yes | Generator running status for GEN18; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30627 | 30627 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_OpStatus_VAL | Yes | Generator running status for GEN19; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30662 | 30662 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN02 | GCS_G2_OpStatus_VAL | Yes | Generator running status for GEN2; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30067 | 30067 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_OpStatus_VAL | Yes | Generator running status for GEN20; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30697 | 30697 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_OpStatus_VAL | Yes | Generator running status for GEN21; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30732 | 30732 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_OpStatus_VAL | Yes | Generator running status for GEN22; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30767 | 30767 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_OpStatus_VAL | Yes | Generator running status for GEN23; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30802 | 30802 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_OpStatus_VAL | Yes | Generator running status for GEN24; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30837 | 30837 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_OpStatus_VAL | Yes | Generator running status for GEN25; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30872 | 30872 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_OpStatus_VAL | Yes | Generator running status for GEN26; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30907 | 30907 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_OpStatus_VAL | Yes | Generator running status for GEN27; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30942 | 30942 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_OpStatus_VAL | Yes | Generator running status for GEN28; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30977 | 30977 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_OpStatus_VAL | Yes | Generator running status for GEN29; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31012 | 31012 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN03 | GCS_G3_OpStatus_VAL | Yes | Generator running status for GEN3; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30102 | 30102 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_OpStatus_VAL | Yes | Generator running status for GEN30; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31047 | 31047 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_OpStatus_VAL | Yes | Generator running status for GEN31; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31082 | 31082 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_OpStatus_VAL | Yes | Generator running status for GEN32; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31117 | 31117 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_OpStatus_VAL | Yes | Generator running status for GEN33; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31152 | 31152 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_OpStatus_VAL | Yes | Generator running status for GEN34; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31187 | 31187 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_OpStatus_VAL | Yes | Generator running status for GEN35; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31222 | 31222 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_OpStatus_VAL | Yes | Generator running status for GEN36; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31257 | 31257 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_OpStatus_VAL | Yes | Generator running status for GEN37; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31292 | 31292 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_OpStatus_VAL | Yes | Generator running status for GEN38; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31327 | 31327 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_OpStatus_VAL | Yes | Generator running status for GEN39; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31362 | 31362 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN04 | GCS_G4_OpStatus_VAL | Yes | Generator running status for GEN4; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30137 | 30137 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_OpStatus_VAL | Yes | Generator running status for GEN40; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31397 | 31397 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_OpStatus_VAL | Yes | Generator running status for GEN41; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31432 | 31432 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_OpStatus_VAL | Yes | Generator running status for GEN42; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31467 | 31467 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_OpStatus_VAL | Yes | Generator running status for GEN43; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31502 | 31502 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_OpStatus_VAL | Yes | Generator running status for GEN44; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31537 | 31537 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_OpStatus_VAL | Yes | Generator running status for GEN45; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31572 | 31572 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_OpStatus_VAL | Yes | Generator running status for GEN46; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 31607 | 31607 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN05 | GCS_G5_OpStatus_VAL | Yes | Generator running status for GEN5; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30172 | 30172 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN06 | GCS_G6_OpStatus_VAL | Yes | Generator running status for GEN6; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30207 | 30207 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN07 | GCS_G7_OpStatus_VAL | Yes | Generator running status for GEN7; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30242 | 30242 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN08 | GCS_G8_OpStatus_VAL | Yes | Generator running status for GEN8; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30277 | 30277 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN09 | GCS_G9_OpStatus_VAL | Yes | Generator running status for GEN9; 0=unknown, 1=stopped, 2=starting, 3=stopping, 4=running, 5=online | Operation Message | Input Register | 0x04 | 30312 | 30312 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | N/A | N/A | GCS_Enable_CMD | Yes | Global enable for GCS control | Command | Coil | 0x05 | 378 | 378 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Generation Management Control Screens | N/A | N/A | GCS_AlarmAcknowledge_CMD | Yes | Global GCS alarm reset | Command | Coil | 0x05 | 375 | 375 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | N/A | N/A | GMS_Enable_CMD | Yes | Global GMS enable command | Command | Coil | 0x05 | 384 | 384 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Generation Management Control Screens | N/A | N/A | GMS_ControlEnabled_STAT | Yes | GMS Global control enabled status feedback | Operation Message | Discrete Input | 0x02 | 11051 | 11051 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Generation Management Control Screens | QPAC-1 | GEN1 | GMS_G1_GenStartPriority_VAL | Yes | GMS running priority for GEN1 | Operation Message | Input Register | 0x04 | 30031 | 30031 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN10 | GMS_G10_GenStartPriority_VAL | Yes | GMS running priority for GEN10 | Operation Message | Input Register | 0x04 | 30346 | 30346 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN11 | GMS_G11_GenStartPriority_VAL | Yes | GMS running priority for GEN11 | Operation Message | Input Register | 0x04 | 30381 | 30381 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN12 | GMS_G12_GenStartPriority_VAL | Yes | GMS running priority for GEN12 | Operation Message | Input Register | 0x04 | 30416 | 30416 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN13 | GMS_G13_GenStartPriority_VAL | Yes | GMS running priority for GEN13 | Operation Message | Input Register | 0x04 | 30451 | 30451 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN14 | GMS_G14_GenStartPriority_VAL | Yes | GMS running priority for GEN14 | Operation Message | Input Register | 0x04 | 30486 | 30486 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN15 | GMS_G15_GenStartPriority_VAL | Yes | GMS running priority for GEN15 | Operation Message | Input Register | 0x04 | 30521 | 30521 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-4 | GEN16 | GMS_G16_GenStartPriority_VAL | Yes | GMS running priority for GEN16 | Operation Message | Input Register | 0x04 | 30556 | 30556 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN17 | GMS_G17_GenStartPriority_VAL | Yes | GMS running priority for GEN17 | Operation Message | Input Register | 0x04 | 30591 | 30591 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN18 | GMS_G18_GenStartPriority_VAL | Yes | GMS running priority for GEN18 | Operation Message | Input Register | 0x04 | 30626 | 30626 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN19 | GMS_G19_GenStartPriority_VAL | Yes | GMS running priority for GEN19 | Operation Message | Input Register | 0x04 | 30661 | 30661 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN2 | GMS_G2_GenStartPriority_VAL | Yes | GMS running priority for GEN2 | Operation Message | Input Register | 0x04 | 30066 | 30066 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-5 | GEN20 | GMS_G20_GenStartPriority_VAL | Yes | GMS running priority for GEN20 | Operation Message | Input Register | 0x04 | 30696 | 30696 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN21 | GMS_G21_GenStartPriority_VAL | Yes | GMS running priority for GEN21 | Operation Message | Input Register | 0x04 | 30731 | 30731 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN22 | GMS_G22_GenStartPriority_VAL | Yes | GMS running priority for GEN22 | Operation Message | Input Register | 0x04 | 30766 | 30766 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN23 | GMS_G23_GenStartPriority_VAL | Yes | GMS running priority for GEN23 | Operation Message | Input Register | 0x04 | 30801 | 30801 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-6 | GEN24 | GMS_G24_GenStartPriority_VAL | Yes | GMS running priority for GEN24 | Operation Message | Input Register | 0x04 | 30836 | 30836 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN25 | GMS_G25_GenStartPriority_VAL | Yes | GMS running priority for GEN25 | Operation Message | Input Register | 0x04 | 30871 | 30871 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN26 | GMS_G26_GenStartPriority_VAL | Yes | GMS running priority for GEN26 | Operation Message | Input Register | 0x04 | 30906 | 30906 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN27 | GMS_G27_GenStartPriority_VAL | Yes | GMS running priority for GEN27 | Operation Message | Input Register | 0x04 | 30941 | 30941 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-7 | GEN28 | GMS_G28_GenStartPriority_VAL | Yes | GMS running priority for GEN28 | Operation Message | Input Register | 0x04 | 30976 | 30976 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN29 | GMS_G29_GenStartPriority_VAL | Yes | GMS running priority for GEN29 | Operation Message | Input Register | 0x04 | 31011 | 31011 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN3 | GMS_G3_GenStartPriority_VAL | Yes | GMS running priority for GEN3 | Operation Message | Input Register | 0x04 | 30101 | 30101 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN30 | GMS_G30_GenStartPriority_VAL | Yes | GMS running priority for GEN30 | Operation Message | Input Register | 0x04 | 31046 | 31046 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN31 | GMS_G31_GenStartPriority_VAL | Yes | GMS running priority for GEN31 | Operation Message | Input Register | 0x04 | 31081 | 31081 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-8 | GEN32 | GMS_G32_GenStartPriority_VAL | Yes | GMS running priority for GEN32 | Operation Message | Input Register | 0x04 | 31116 | 31116 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN33 | GMS_G33_GenStartPriority_VAL | Yes | GMS running priority for GEN33 | Operation Message | Input Register | 0x04 | 31151 | 31151 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN34 | GMS_G34_GenStartPriority_VAL | Yes | GMS running priority for GEN34 | Operation Message | Input Register | 0x04 | 31186 | 31186 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN35 | GMS_G35_GenStartPriority_VAL | Yes | GMS running priority for GEN35 | Operation Message | Input Register | 0x04 | 31221 | 31221 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-9 | GEN36 | GMS_G36_GenStartPriority_VAL | Yes | GMS running priority for GEN36 | Operation Message | Input Register | 0x04 | 31256 | 31256 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN37 | GMS_G37_GenStartPriority_VAL | Yes | GMS running priority for GEN37 | Operation Message | Input Register | 0x04 | 31291 | 31291 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN38 | GMS_G38_GenStartPriority_VAL | Yes | GMS running priority for GEN38 | Operation Message | Input Register | 0x04 | 31326 | 31326 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN39 | GMS_G39_GenStartPriority_VAL | Yes | GMS running priority for GEN39 | Operation Message | Input Register | 0x04 | 31361 | 31361 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN4 | GMS_G4_GenStartPriority_VAL | Yes | GMS running priority for GEN4 | Operation Message | Input Register | 0x04 | 30136 | 30136 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-10 | GEN40 | GMS_G40_GenStartPriority_VAL | Yes | GMS running priority for GEN40 | Operation Message | Input Register | 0x04 | 31396 | 31396 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN41 | GMS_G41_GenStartPriority_VAL | Yes | GMS running priority for GEN41 | Operation Message | Input Register | 0x04 | 31431 | 31431 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN42 | GMS_G42_GenStartPriority_VAL | Yes | GMS running priority for GEN42 | Operation Message | Input Register | 0x04 | 31466 | 31466 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN43 | GMS_G43_GenStartPriority_VAL | Yes | GMS running priority for GEN43 | Operation Message | Input Register | 0x04 | 31501 | 31501 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-11 | GEN44 | GMS_G44_GenStartPriority_VAL | Yes | GMS running priority for GEN44 | Operation Message | Input Register | 0x04 | 31536 | 31536 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-12 | GEN45 | GMS_G45_GenStartPriority_VAL | Yes | GMS running priority for GEN45 | Operation Message | Input Register | 0x04 | 31571 | 31571 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-12 | GEN46 | GMS_G46_GenStartPriority_VAL | Yes | GMS running priority for GEN46 | Operation Message | Input Register | 0x04 | 31606 | 31606 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN5 | GMS_G5_GenStartPriority_VAL | Yes | GMS running priority for GEN5 | Operation Message | Input Register | 0x04 | 30171 | 30171 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN6 | GMS_G6_GenStartPriority_VAL | Yes | GMS running priority for GEN6 | Operation Message | Input Register | 0x04 | 30206 | 30206 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN7 | GMS_G7_GenStartPriority_VAL | Yes | GMS running priority for GEN7 | Operation Message | Input Register | 0x04 | 30241 | 30241 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-2 | GEN8 | GMS_G8_GenStartPriority_VAL | Yes | GMS running priority for GEN8 | Operation Message | Input Register | 0x04 | 30276 | 30276 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-3 | GEN9 | GMS_G9_GenStartPriority_VAL | Yes | GMS running priority for GEN9 | Operation Message | Input Register | 0x04 | 30311 | 30311 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_Start_CMD | Yes | Manual Start command for GEN1 | Command | Coil | 0x05 | 1 | 1 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_Start_CMD | Yes | Manual Start command for GEN10 | Command | Coil | 0x05 | 73 | 73 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_Start_CMD | Yes | Manual Start command for GEN11 | Command | Coil | 0x05 | 81 | 81 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_Start_CMD | Yes | Manual Start command for GEN12 | Command | Coil | 0x05 | 89 | 89 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_Start_CMD | Yes | Manual Start command for GEN13 | Command | Coil | 0x05 | 97 | 97 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_Start_CMD | Yes | Manual Start command for GEN14 | Command | Coil | 0x05 | 105 | 105 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_Start_CMD | Yes | Manual Start command for GEN15 | Command | Coil | 0x05 | 113 | 113 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_Start_CMD | Yes | Manual Start command for GEN16 | Command | Coil | 0x05 | 121 | 121 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_Start_CMD | Yes | Manual Start command for GEN17 | Command | Coil | 0x05 | 129 | 129 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_Start_CMD | Yes | Manual Start command for GEN18 | Command | Coil | 0x05 | 137 | 137 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_Start_CMD | Yes | Manual Start command for GEN19 | Command | Coil | 0x05 | 145 | 145 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_Start_CMD | Yes | Manual Start command for GEN2 | Command | Coil | 0x05 | 9 | 9 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_Start_CMD | Yes | Manual Start command for GEN20 | Command | Coil | 0x05 | 153 | 153 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_Start_CMD | Yes | Manual Start command for GEN21 | Command | Coil | 0x05 | 161 | 161 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_Start_CMD | Yes | Manual Start command for GEN22 | Command | Coil | 0x05 | 169 | 169 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_Start_CMD | Yes | Manual Start command for GEN23 | Command | Coil | 0x05 | 177 | 177 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_Start_CMD | Yes | Manual Start command for GEN24 | Command | Coil | 0x05 | 185 | 185 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_Start_CMD | Yes | Manual Start command for GEN25 | Command | Coil | 0x05 | 193 | 193 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_Start_CMD | Yes | Manual Start command for GEN26 | Command | Coil | 0x05 | 201 | 201 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_Start_CMD | Yes | Manual Start command for GEN27 | Command | Coil | 0x05 | 209 | 209 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_Start_CMD | Yes | Manual Start command for GEN28 | Command | Coil | 0x05 | 217 | 217 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_Start_CMD | Yes | Manual Start command for GEN29 | Command | Coil | 0x05 | 225 | 225 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_Start_CMD | Yes | Manual Start command for GEN3 | Command | Coil | 0x05 | 17 | 17 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_Start_CMD | Yes | Manual Start command for GEN30 | Command | Coil | 0x05 | 233 | 233 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_Start_CMD | Yes | Manual Start command for GEN31 | Command | Coil | 0x05 | 241 | 241 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_Start_CMD | Yes | Manual Start command for GEN32 | Command | Coil | 0x05 | 249 | 249 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_Start_CMD | Yes | Manual Start command for GEN33 | Command | Coil | 0x05 | 257 | 257 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_Start_CMD | Yes | Manual Start command for GEN34 | Command | Coil | 0x05 | 265 | 265 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_Start_CMD | Yes | Manual Start command for GEN35 | Command | Coil | 0x05 | 273 | 273 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_Start_CMD | Yes | Manual Start command for GEN36 | Command | Coil | 0x05 | 281 | 281 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_Start_CMD | Yes | Manual Start command for GEN37 | Command | Coil | 0x05 | 289 | 289 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_Start_CMD | Yes | Manual Start command for GEN38 | Command | Coil | 0x05 | 297 | 297 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_Start_CMD | Yes | Manual Start command for GEN39 | Command | Coil | 0x05 | 305 | 305 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_Start_CMD | Yes | Manual Start command for GEN4 | Command | Coil | 0x05 | 25 | 25 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_Start_CMD | Yes | Manual Start command for GEN40 | Command | Coil | 0x05 | 313 | 313 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_Start_CMD | Yes | Manual Start command for GEN41 | Command | Coil | 0x05 | 321 | 321 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_Start_CMD | Yes | Manual Start command for GEN42 | Command | Coil | 0x05 | 329 | 329 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_Start_CMD | Yes | Manual Start command for GEN43 | Command | Coil | 0x05 | 337 | 337 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_Start_CMD | Yes | Manual Start command for GEN44 | Command | Coil | 0x05 | 345 | 345 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_Start_CMD | Yes | Manual Start command for GEN45 | Command | Coil | 0x05 | 353 | 353 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_Start_CMD | Yes | Manual Start command for GEN46 | Command | Coil | 0x05 | 361 | 361 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_Start_CMD | Yes | Manual Start command for GEN5 | Command | Coil | 0x05 | 33 | 33 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_Start_CMD | Yes | Manual Start command for GEN6 | Command | Coil | 0x05 | 41 | 41 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_Start_CMD | Yes | Manual Start command for GEN7 | Command | Coil | 0x05 | 49 | 49 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_Start_CMD | Yes | Manual Start command for GEN8 | Command | Coil | 0x05 | 57 | 57 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_Start_CMD | Yes | Manual Start command for GEN9 | Command | Coil | 0x05 | 65 | 65 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_Stop_CMD | Yes | Manual Stop command for GEN1 | Command | Coil | 0x05 | 2 | 2 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_Stop_CMD | Yes | Manual Stop command for GEN10 | Command | Coil | 0x05 | 74 | 74 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_Stop_CMD | Yes | Manual Stop command for GEN11 | Command | Coil | 0x05 | 82 | 82 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_Stop_CMD | Yes | Manual Stop command for GEN12 | Command | Coil | 0x05 | 90 | 90 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_Stop_CMD | Yes | Manual Stop command for GEN13 | Command | Coil | 0x05 | 98 | 98 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_Stop_CMD | Yes | Manual Stop command for GEN14 | Command | Coil | 0x05 | 106 | 106 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_Stop_CMD | Yes | Manual Stop command for GEN15 | Command | Coil | 0x05 | 114 | 114 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_Stop_CMD | Yes | Manual Stop command for GEN16 | Command | Coil | 0x05 | 122 | 122 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_Stop_CMD | Yes | Manual Stop command for GEN17 | Command | Coil | 0x05 | 130 | 130 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_Stop_CMD | Yes | Manual Stop command for GEN18 | Command | Coil | 0x05 | 138 | 138 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_Stop_CMD | Yes | Manual Stop command for GEN19 | Command | Coil | 0x05 | 146 | 146 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_Stop_CMD | Yes | Manual Stop command for GEN2 | Command | Coil | 0x05 | 10 | 10 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_Stop_CMD | Yes | Manual Stop command for GEN20 | Command | Coil | 0x05 | 154 | 154 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_Stop_CMD | Yes | Manual Stop command for GEN21 | Command | Coil | 0x05 | 162 | 162 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_Stop_CMD | Yes | Manual Stop command for GEN22 | Command | Coil | 0x05 | 170 | 170 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_Stop_CMD | Yes | Manual Stop command for GEN23 | Command | Coil | 0x05 | 178 | 178 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_Stop_CMD | Yes | Manual Stop command for GEN24 | Command | Coil | 0x05 | 186 | 186 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_Stop_CMD | Yes | Manual Stop command for GEN25 | Command | Coil | 0x05 | 194 | 194 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_Stop_CMD | Yes | Manual Stop command for GEN26 | Command | Coil | 0x05 | 202 | 202 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_Stop_CMD | Yes | Manual Stop command for GEN27 | Command | Coil | 0x05 | 210 | 210 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_Stop_CMD | Yes | Manual Stop command for GEN28 | Command | Coil | 0x05 | 218 | 218 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_Stop_CMD | Yes | Manual Stop command for GEN29 | Command | Coil | 0x05 | 226 | 226 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_Stop_CMD | Yes | Manual Stop command for GEN3 | Command | Coil | 0x05 | 18 | 18 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_Stop_CMD | Yes | Manual Stop command for GEN30 | Command | Coil | 0x05 | 234 | 234 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_Stop_CMD | Yes | Manual Stop command for GEN31 | Command | Coil | 0x05 | 242 | 242 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_Stop_CMD | Yes | Manual Stop command for GEN32 | Command | Coil | 0x05 | 250 | 250 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_Stop_CMD | Yes | Manual Stop command for GEN33 | Command | Coil | 0x05 | 258 | 258 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_Stop_CMD | Yes | Manual Stop command for GEN34 | Command | Coil | 0x05 | 266 | 266 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_Stop_CMD | Yes | Manual Stop command for GEN35 | Command | Coil | 0x05 | 274 | 274 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_Stop_CMD | Yes | Manual Stop command for GEN36 | Command | Coil | 0x05 | 282 | 282 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_Stop_CMD | Yes | Manual Stop command for GEN37 | Command | Coil | 0x05 | 290 | 290 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_Stop_CMD | Yes | Manual Stop command for GEN38 | Command | Coil | 0x05 | 298 | 298 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_Stop_CMD | Yes | Manual Stop command for GEN39 | Command | Coil | 0x05 | 306 | 306 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_Stop_CMD | Yes | Manual Stop command for GEN4 | Command | Coil | 0x05 | 26 | 26 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_Stop_CMD | Yes | Manual Stop command for GEN40 | Command | Coil | 0x05 | 314 | 314 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_Stop_CMD | Yes | Manual Stop command for GEN41 | Command | Coil | 0x05 | 322 | 322 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_Stop_CMD | Yes | Manual Stop command for GEN42 | Command | Coil | 0x05 | 330 | 330 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_Stop_CMD | Yes | Manual Stop command for GEN43 | Command | Coil | 0x05 | 338 | 338 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_Stop_CMD | Yes | Manual Stop command for GEN44 | Command | Coil | 0x05 | 346 | 346 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_Stop_CMD | Yes | Manual Stop command for GEN45 | Command | Coil | 0x05 | 354 | 354 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_Stop_CMD | Yes | Manual Stop command for GEN46 | Command | Coil | 0x05 | 362 | 362 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_Stop_CMD | Yes | Manual Stop command for GEN5 | Command | Coil | 0x05 | 34 | 34 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_Stop_CMD | Yes | Manual Stop command for GEN6 | Command | Coil | 0x05 | 42 | 42 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_Stop_CMD | Yes | Manual Stop command for GEN7 | Command | Coil | 0x05 | 50 | 50 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_Stop_CMD | Yes | Manual Stop command for GEN8 | Command | Coil | 0x05 | 58 | 58 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_Stop_CMD | Yes | Manual Stop command for GEN9 | Command | Coil | 0x05 | 66 | 66 | 1 | Boolean | Yes | N/A | Pulse | N/A
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_ControlEnabled_STAT | Yes | MVAR control enabled for GEN1 | Operation Message | Discrete Input | 0x02 | 10012 | 10012 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_ControlEnabled_STAT | Yes | MVAR control enabled for GEN10 | Operation Message | Discrete Input | 0x02 | 10201 | 10201 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_ControlEnabled_STAT | Yes | MVAR control enabled for GEN11 | Operation Message | Discrete Input | 0x02 | 10222 | 10222 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_ControlEnabled_STAT | Yes | MVAR control enabled for GEN12 | Operation Message | Discrete Input | 0x02 | 10243 | 10243 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_ControlEnabled_STAT | Yes | MVAR control enabled for GEN13 | Operation Message | Discrete Input | 0x02 | 10264 | 10264 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_ControlEnabled_STAT | Yes | MVAR control enabled for GEN14 | Operation Message | Discrete Input | 0x02 | 10285 | 10285 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_ControlEnabled_STAT | Yes | MVAR control enabled for GEN15 | Operation Message | Discrete Input | 0x02 | 10306 | 10306 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_ControlEnabled_STAT | Yes | MVAR control enabled for GEN16 | Operation Message | Discrete Input | 0x02 | 10327 | 10327 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_ControlEnabled_STAT | Yes | MVAR control enabled for GEN17 | Operation Message | Discrete Input | 0x02 | 10348 | 10348 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_ControlEnabled_STAT | Yes | MVAR control enabled for GEN18 | Operation Message | Discrete Input | 0x02 | 10369 | 10369 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_ControlEnabled_STAT | Yes | MVAR control enabled for GEN19 | Operation Message | Discrete Input | 0x02 | 10390 | 10390 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-1 | G2 | VCS_G2_ControlEnabled_STAT | Yes | MVAR control enabled for GEN2 | Operation Message | Discrete Input | 0x02 | 10033 | 10033 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-5 | G20 | VCS_G20_ControlEnabled_STAT | Yes | MVAR control enabled for GEN20 | Operation Message | Discrete Input | 0x02 | 10411 | 10411 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-6 | G21 | VCS_G21_ControlEnabled_STAT | Yes | MVAR control enabled for GEN21 | Operation Message | Discrete Input | 0x02 | 10432 | 10432 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-6 | G22 | VCS_G22_ControlEnabled_STAT | Yes | MVAR control enabled for GEN22 | Operation Message | Discrete Input | 0x02 | 10453 | 10453 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-6 | G23 | VCS_G23_ControlEnabled_STAT | Yes | MVAR control enabled for GEN23 | Operation Message | Discrete Input | 0x02 | 10474 | 10474 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-6 | G24 | VCS_G24_ControlEnabled_STAT | Yes | MVAR control enabled for GEN24 | Operation Message | Discrete Input | 0x02 | 10495 | 10495 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-7 | G25 | VCS_G25_ControlEnabled_STAT | Yes | MVAR control enabled for GEN25 | Operation Message | Discrete Input | 0x02 | 10516 | 10516 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-7 | G26 | VCS_G26_ControlEnabled_STAT | Yes | MVAR control enabled for GEN26 | Operation Message | Discrete Input | 0x02 | 10537 | 10537 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-7 | G27 | VCS_G27_ControlEnabled_STAT | Yes | MVAR control enabled for GEN27 | Operation Message | Discrete Input | 0x02 | 10558 | 10558 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-7 | G28 | VCS_G28_ControlEnabled_STAT | Yes | MVAR control enabled for GEN28 | Operation Message | Discrete Input | 0x02 | 10579 | 10579 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-8 | G29 | VCS_G29_ControlEnabled_STAT | Yes | MVAR control enabled for GEN29 | Operation Message | Discrete Input | 0x02 | 10600 | 10600 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-1 | G3 | VCS_G3_ControlEnabled_STAT | Yes | MVAR control enabled for GEN3 | Operation Message | Discrete Input | 0x02 | 10054 | 10054 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-8 | G30 | VCS_G30_ControlEnabled_STAT | Yes | MVAR control enabled for GEN30 | Operation Message | Discrete Input | 0x02 | 10621 | 10621 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-8 | G31 | VCS_G31_ControlEnabled_STAT | Yes | MVAR control enabled for GEN31 | Operation Message | Discrete Input | 0x02 | 10642 | 10642 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-8 | G32 | VCS_G32_ControlEnabled_STAT | Yes | MVAR control enabled for GEN32 | Operation Message | Discrete Input | 0x02 | 10663 | 10663 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-9 | G33 | VCS_G33_ControlEnabled_STAT | Yes | MVAR control enabled for GEN33 | Operation Message | Discrete Input | 0x02 | 10684 | 10684 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-9 | G34 | VCS_G34_ControlEnabled_STAT | Yes | MVAR control enabled for GEN34 | Operation Message | Discrete Input | 0x02 | 10705 | 10705 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-9 | G35 | VCS_G35_ControlEnabled_STAT | Yes | MVAR control enabled for GEN35 | Operation Message | Discrete Input | 0x02 | 10726 | 10726 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-9 | G36 | VCS_G36_ControlEnabled_STAT | Yes | MVAR control enabled for GEN36 | Operation Message | Discrete Input | 0x02 | 10747 | 10747 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-10 | G37 | VCS_G37_ControlEnabled_STAT | Yes | MVAR control enabled for GEN37 | Operation Message | Discrete Input | 0x02 | 10768 | 10768 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-10 | G38 | VCS_G38_ControlEnabled_STAT | Yes | MVAR control enabled for GEN38 | Operation Message | Discrete Input | 0x02 | 10789 | 10789 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-10 | G39 | VCS_G39_ControlEnabled_STAT | Yes | MVAR control enabled for GEN39 | Operation Message | Discrete Input | 0x02 | 10810 | 10810 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-1 | G4 | VCS_G4_ControlEnabled_STAT | Yes | MVAR control enabled for GEN4 | Operation Message | Discrete Input | 0x02 | 10075 | 10075 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-10 | G40 | VCS_G40_ControlEnabled_STAT | Yes | MVAR control enabled for GEN40 | Operation Message | Discrete Input | 0x02 | 10831 | 10831 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-11 | G41 | VCS_G41_ControlEnabled_STAT | Yes | MVAR control enabled for GEN41 | Operation Message | Discrete Input | 0x02 | 10852 | 10852 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-11 | G42 | VCS_G42_ControlEnabled_STAT | Yes | MVAR control enabled for GEN42 | Operation Message | Discrete Input | 0x02 | 10873 | 10873 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-11 | G43 | VCS_G43_ControlEnabled_STAT | Yes | MVAR control enabled for GEN43 | Operation Message | Discrete Input | 0x02 | 10894 | 10894 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-11 | G44 | VCS_G44_ControlEnabled_STAT | Yes | MVAR control enabled for GEN44 | Operation Message | Discrete Input | 0x02 | 10915 | 10915 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-12 | G45 | VCS_G45_ControlEnabled_STAT | Yes | MVAR control enabled for GEN45 | Operation Message | Discrete Input | 0x02 | 10936 | 10936 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-12 | G46 | VCS_G46_ControlEnabled_STAT | Yes | MVAR control enabled for GEN46 | Operation Message | Discrete Input | 0x02 | 10957 | 10957 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-2 | G5 | VCS_G5_ControlEnabled_STAT | Yes | MVAR control enabled for GEN5 | Operation Message | Discrete Input | 0x02 | 10096 | 10096 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-2 | G6 | VCS_G6_ControlEnabled_STAT | Yes | MVAR control enabled for GEN6 | Operation Message | Discrete Input | 0x02 | 10117 | 10117 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-2 | G7 | VCS_G7_ControlEnabled_STAT | Yes | MVAR control enabled for GEN7 | Operation Message | Discrete Input | 0x02 | 10138 | 10138 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-2 | G8 | VCS_G8_ControlEnabled_STAT | Yes | MVAR control enabled for GEN8 | Operation Message | Discrete Input | 0x02 | 10159 | 10159 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-3 | G9 | VCS_G9_ControlEnabled_STAT | Yes | MVAR control enabled for GEN9 | Operation Message | Discrete Input | 0x02 | 10180 | 10180 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_ControlMode_VAL | Yes | MVAR control mode of G1; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30030 | 30030 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_ControlMode_VAL | Yes | MVAR control mode of G10; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30345 | 30345 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_ControlMode_VAL | Yes | MVAR control mode of G11; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30380 | 30380 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_ControlMode_VAL | Yes | MVAR control mode of G12; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30415 | 30415 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_ControlMode_VAL | Yes | MVAR control mode of G13; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30450 | 30450 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_ControlMode_VAL | Yes | MVAR control mode of G14; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30485 | 30485 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_ControlMode_VAL | Yes | MVAR control mode of G15; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30520 | 30520 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_ControlMode_VAL | Yes | MVAR control mode of G16; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30555 | 30555 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_ControlMode_VAL | Yes | MVAR control mode of G17; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30590 | 30590 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_ControlMode_VAL | Yes | MVAR control mode of G18; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30625 | 30625 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_ControlMode_VAL | Yes | MVAR control mode of G19; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30660 | 30660 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_ControlMode_VAL | Yes | MVAR control mode of G2; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30065 | 30065 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_ControlMode_VAL | Yes | MVAR control mode of G20; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30695 | 30695 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_ControlMode_VAL | Yes | MVAR control mode of G21; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30730 | 30730 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_ControlMode_VAL | Yes | MVAR control mode of G22; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30765 | 30765 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_ControlMode_VAL | Yes | MVAR control mode of G23; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30800 | 30800 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_ControlMode_VAL | Yes | MVAR control mode of G24; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30835 | 30835 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_ControlMode_VAL | Yes | MVAR control mode of G25; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30870 | 30870 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_ControlMode_VAL | Yes | MVAR control mode of G26; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30905 | 30905 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_ControlMode_VAL | Yes | MVAR control mode of G27; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30940 | 30940 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_ControlMode_VAL | Yes | MVAR control mode of G28; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30975 | 30975 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_ControlMode_VAL | Yes | MVAR control mode of G29; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31010 | 31010 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_ControlMode_VAL | Yes | MVAR control mode of G3; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30100 | 30100 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_ControlMode_VAL | Yes | MVAR control mode of G30; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31045 | 31045 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_ControlMode_VAL | Yes | MVAR control mode of G31; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31080 | 31080 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_ControlMode_VAL | Yes | MVAR control mode of G32; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31115 | 31115 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_ControlMode_VAL | Yes | MVAR control mode of G33; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31150 | 31150 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_ControlMode_VAL | Yes | MVAR control mode of G34; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31185 | 31185 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_ControlMode_VAL | Yes | MVAR control mode of G35; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31220 | 31220 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_ControlMode_VAL | Yes | MVAR control mode of G36; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31255 | 31255 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_ControlMode_VAL | Yes | MVAR control mode of G37; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31290 | 31290 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_ControlMode_VAL | Yes | MVAR control mode of G38; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31325 | 31325 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_ControlMode_VAL | Yes | MVAR control mode of G39; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31360 | 31360 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_ControlMode_VAL | Yes | MVAR control mode of G4; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30135 | 30135 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_ControlMode_VAL | Yes | MVAR control mode of G40; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31395 | 31395 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_ControlMode_VAL | Yes | MVAR control mode of G41; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31430 | 31430 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_ControlMode_VAL | Yes | MVAR control mode of G42; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31465 | 31465 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_ControlMode_VAL | Yes | MVAR control mode of G43; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31500 | 31500 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_ControlMode_VAL | Yes | MVAR control mode of G44; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31535 | 31535 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_ControlMode_VAL | Yes | MVAR control mode of G45; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31570 | 31570 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_ControlMode_VAL | Yes | MVAR control mode of G46; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 31605 | 31605 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_ControlMode_VAL | Yes | MVAR control mode of G5; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30170 | 30170 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_ControlMode_VAL | Yes | MVAR control mode of G6; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30205 | 30205 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_ControlMode_VAL | Yes | MVAR control mode of G7; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30240 | 30240 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_ControlMode_VAL | Yes | MVAR control mode of G8; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30275 | 30275 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_ControlMode_VAL | Yes | MVAR control mode of G9; 0=unknown, 1=constantQ, 2=constantPF, 3=constantV, 4=Vdroop, 5=OFF | Operation Message | Input Register | 0x04 | 30310 | 30310 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_ControlEnabled_STAT | Yes | MW control enabled for GEN1 | Operation Message | Discrete Input | 0x02 | 10001 | 10001 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_ControlEnabled_STAT | Yes | MW control enabled for GEN10 | Operation Message | Discrete Input | 0x02 | 10190 | 10190 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_ControlEnabled_STAT | Yes | MW control enabled for GEN11 | Operation Message | Discrete Input | 0x02 | 10211 | 10211 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_ControlEnabled_STAT | Yes | MW control enabled for GEN12 | Operation Message | Discrete Input | 0x02 | 10232 | 10232 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_ControlEnabled_STAT | Yes | MW control enabled for GEN13 | Operation Message | Discrete Input | 0x02 | 10253 | 10253 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_ControlEnabled_STAT | Yes | MW control enabled for GEN14 | Operation Message | Discrete Input | 0x02 | 10274 | 10274 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_ControlEnabled_STAT | Yes | MW control enabled for GEN15 | Operation Message | Discrete Input | 0x02 | 10295 | 10295 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_ControlEnabled_STAT | Yes | MW control enabled for GEN16 | Operation Message | Discrete Input | 0x02 | 10316 | 10316 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_ControlEnabled_STAT | Yes | MW control enabled for GEN17 | Operation Message | Discrete Input | 0x02 | 10337 | 10337 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_ControlEnabled_STAT | Yes | MW control enabled for GEN18 | Operation Message | Discrete Input | 0x02 | 10358 | 10358 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_ControlEnabled_STAT | Yes | MW control enabled for GEN19 | Operation Message | Discrete Input | 0x02 | 10379 | 10379 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_ControlEnabled_STAT | Yes | MW control enabled for GEN2 | Operation Message | Discrete Input | 0x02 | 10022 | 10022 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_ControlEnabled_STAT | Yes | MW control enabled for GEN20 | Operation Message | Discrete Input | 0x02 | 10400 | 10400 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_ControlEnabled_STAT | Yes | MW control enabled for GEN21 | Operation Message | Discrete Input | 0x02 | 10421 | 10421 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_ControlEnabled_STAT | Yes | MW control enabled for GEN22 | Operation Message | Discrete Input | 0x02 | 10442 | 10442 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_ControlEnabled_STAT | Yes | MW control enabled for GEN23 | Operation Message | Discrete Input | 0x02 | 10463 | 10463 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_ControlEnabled_STAT | Yes | MW control enabled for GEN24 | Operation Message | Discrete Input | 0x02 | 10484 | 10484 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_ControlEnabled_STAT | Yes | MW control enabled for GEN25 | Operation Message | Discrete Input | 0x02 | 10505 | 10505 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_ControlEnabled_STAT | Yes | MW control enabled for GEN26 | Operation Message | Discrete Input | 0x02 | 10526 | 10526 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_ControlEnabled_STAT | Yes | MW control enabled for GEN27 | Operation Message | Discrete Input | 0x02 | 10547 | 10547 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_ControlEnabled_STAT | Yes | MW control enabled for GEN28 | Operation Message | Discrete Input | 0x02 | 10568 | 10568 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_ControlEnabled_STAT | Yes | MW control enabled for GEN29 | Operation Message | Discrete Input | 0x02 | 10589 | 10589 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_ControlEnabled_STAT | Yes | MW control enabled for GEN3 | Operation Message | Discrete Input | 0x02 | 10043 | 10043 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_ControlEnabled_STAT | Yes | MW control enabled for GEN30 | Operation Message | Discrete Input | 0x02 | 10610 | 10610 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_ControlEnabled_STAT | Yes | MW control enabled for GEN31 | Operation Message | Discrete Input | 0x02 | 10631 | 10631 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_ControlEnabled_STAT | Yes | MW control enabled for GEN32 | Operation Message | Discrete Input | 0x02 | 10652 | 10652 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_ControlEnabled_STAT | Yes | MW control enabled for GEN33 | Operation Message | Discrete Input | 0x02 | 10673 | 10673 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_ControlEnabled_STAT | Yes | MW control enabled for GEN34 | Operation Message | Discrete Input | 0x02 | 10694 | 10694 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_ControlEnabled_STAT | Yes | MW control enabled for GEN35 | Operation Message | Discrete Input | 0x02 | 10715 | 10715 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_ControlEnabled_STAT | Yes | MW control enabled for GEN36 | Operation Message | Discrete Input | 0x02 | 10736 | 10736 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_ControlEnabled_STAT | Yes | MW control enabled for GEN37 | Operation Message | Discrete Input | 0x02 | 10757 | 10757 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_ControlEnabled_STAT | Yes | MW control enabled for GEN38 | Operation Message | Discrete Input | 0x02 | 10778 | 10778 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_ControlEnabled_STAT | Yes | MW control enabled for GEN39 | Operation Message | Discrete Input | 0x02 | 10799 | 10799 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_ControlEnabled_STAT | Yes | MW control enabled for GEN4 | Operation Message | Discrete Input | 0x02 | 10064 | 10064 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_ControlEnabled_STAT | Yes | MW control enabled for GEN40 | Operation Message | Discrete Input | 0x02 | 10820 | 10820 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_ControlEnabled_STAT | Yes | MW control enabled for GEN41 | Operation Message | Discrete Input | 0x02 | 10841 | 10841 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_ControlEnabled_STAT | Yes | MW control enabled for GEN42 | Operation Message | Discrete Input | 0x02 | 10862 | 10862 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_ControlEnabled_STAT | Yes | MW control enabled for GEN43 | Operation Message | Discrete Input | 0x02 | 10883 | 10883 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_ControlEnabled_STAT | Yes | MW control enabled for GEN44 | Operation Message | Discrete Input | 0x02 | 10904 | 10904 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_ControlEnabled_STAT | Yes | MW control enabled for GEN45 | Operation Message | Discrete Input | 0x02 | 10925 | 10925 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_ControlEnabled_STAT | Yes | MW control enabled for GEN46 | Operation Message | Discrete Input | 0x02 | 10946 | 10946 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_ControlEnabled_STAT | Yes | MW control enabled for GEN5 | Operation Message | Discrete Input | 0x02 | 10085 | 10085 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_ControlEnabled_STAT | Yes | MW control enabled for GEN6 | Operation Message | Discrete Input | 0x02 | 10106 | 10106 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_ControlEnabled_STAT | Yes | MW control enabled for GEN7 | Operation Message | Discrete Input | 0x02 | 10127 | 10127 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_ControlEnabled_STAT | Yes | MW control enabled for GEN8 | Operation Message | Discrete Input | 0x02 | 10148 | 10148 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_ControlEnabled_STAT | Yes | MW control enabled for GEN9 | Operation Message | Discrete Input | 0x02 | 10169 | 10169 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_ControlMode_VAL | Yes | MW control mode of G1; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30029 | 30029 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_ControlMode_VAL | Yes | MW control mode of G10; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30344 | 30344 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_ControlMode_VAL | Yes | MW control mode of G11; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30379 | 30379 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_ControlMode_VAL | Yes | MW control mode of G12; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30414 | 30414 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_ControlMode_VAL | Yes | MW control mode of G13; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30449 | 30449 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_ControlMode_VAL | Yes | MW control mode of G14; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30484 | 30484 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_ControlMode_VAL | Yes | MW control mode of G15; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30519 | 30519 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_ControlMode_VAL | Yes | MW control mode of G16; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30554 | 30554 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_ControlMode_VAL | Yes | MW control mode of G17; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30589 | 30589 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_ControlMode_VAL | Yes | MW control mode of G18; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30624 | 30624 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_ControlMode_VAL | Yes | MW control mode of G19; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30659 | 30659 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_ControlMode_VAL | Yes | MW control mode of G2; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30064 | 30064 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_ControlMode_VAL | Yes | MW control mode of G20; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30694 | 30694 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_ControlMode_VAL | Yes | MW control mode of G21; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30729 | 30729 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_ControlMode_VAL | Yes | MW control mode of G22; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30764 | 30764 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_ControlMode_VAL | Yes | MW control mode of G23; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30799 | 30799 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_ControlMode_VAL | Yes | MW control mode of G24; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30834 | 30834 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_ControlMode_VAL | Yes | MW control mode of G25; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30869 | 30869 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_ControlMode_VAL | Yes | MW control mode of G26; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30904 | 30904 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_ControlMode_VAL | Yes | MW control mode of G27; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30939 | 30939 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_ControlMode_VAL | Yes | MW control mode of G28; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30974 | 30974 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_ControlMode_VAL | Yes | MW control mode of G29; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31009 | 31009 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_ControlMode_VAL | Yes | MW control mode of G3; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30099 | 30099 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_ControlMode_VAL | Yes | MW control mode of G30; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31044 | 31044 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_ControlMode_VAL | Yes | MW control mode of G31; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31079 | 31079 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_ControlMode_VAL | Yes | MW control mode of G32; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31114 | 31114 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_ControlMode_VAL | Yes | MW control mode of G33; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31149 | 31149 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_ControlMode_VAL | Yes | MW control mode of G34; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31184 | 31184 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_ControlMode_VAL | Yes | MW control mode of G35; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31219 | 31219 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_ControlMode_VAL | Yes | MW control mode of G36; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31254 | 31254 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_ControlMode_VAL | Yes | MW control mode of G37; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31289 | 31289 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_ControlMode_VAL | Yes | MW control mode of G38; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31324 | 31324 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_ControlMode_VAL | Yes | MW control mode of G39; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31359 | 31359 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_ControlMode_VAL | Yes | MW control mode of G4; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30134 | 30134 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_ControlMode_VAL | Yes | MW control mode of G40; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31394 | 31394 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_ControlMode_VAL | Yes | MW control mode of G41; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31429 | 31429 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_ControlMode_VAL | Yes | MW control mode of G42; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31464 | 31464 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_ControlMode_VAL | Yes | MW control mode of G43; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31499 | 31499 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_ControlMode_VAL | Yes | MW control mode of G44; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31534 | 31534 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_ControlMode_VAL | Yes | MW control mode of G45; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31569 | 31569 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_ControlMode_VAL | Yes | MW control mode of G46; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 31604 | 31604 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_ControlMode_VAL | Yes | MW control mode of G5; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30169 | 30169 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_ControlMode_VAL | Yes | MW control mode of G6; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30204 | 30204 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_ControlMode_VAL | Yes | MW control mode of G7; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30239 | 30239 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_ControlMode_VAL | Yes | MW control mode of G8; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30274 | 30274 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_ControlMode_VAL | Yes | MW control mode of G9; 0=unknown, 1=constantP, 2=constantF, 3=Fdroop, 4=OFF | Operation Message | Input Register | 0x04 | 30309 | 30309 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_DDB_Band_1_VAL | Yes | MW double deadband for GEN1 |  | Input Register | 0x04 | 31651 | 31652 | 2 | Float | No | 32 bit float MSR
N/A | QPAC-12 | ICB-45 | ICB_G45_BreakerStatus_VAL | No | N/A for Node 1 | Operation Message | Input Register | 0x04 | 31575 | 31575 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | QPAC-12 | ICB-46 | ICB_G46_BreakerStatus_VAL | No | N/A for Node 1 | Operation Message | Input Register | 0x04 | 31610 | 31610 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
N/A | N\A | N\A | AGC_GlobalBaseSetpoint_SET | No | Not in use |  | Holding Register | 0x10 | 40599 | 40600 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW | Convert to Spare
Blackstart Sequence | N\A | N\A | BS_NumberOfBlackstartGen_SET | Yes | Not in use |  | Holding Register | 0x06 | 40605 | 40605 | 1 | Int | Yes | 16 bit signed MSB | N/A | N/A
N/A | N\A | N\A | VCS_GlobalBaseSetpoint_SET | No | Not in use |  | Holding Register | 0x10 | 40613 | 40614 | 2 | Float | Yes | 32 bit float MSR | MVAr | 1 Unit = 1 MVAR | Convert to Spare
Generation Management Control Screens | N\A | N\A | GMS_PriorityChangeGENNum_SET | Yes | Number identifier of generator to have its GMS running priority changed |  | Holding Register | 0x06 | 40618 | 40618 | 1 | Int | Yes | 16 bit signed MSB | N/A | N/A
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN1 | Control Setpoint | Holding Register | 0x10 | 40009 | 40010 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN10 | Control Setpoint | Holding Register | 0x10 | 40126 | 40127 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN11 | Control Setpoint | Holding Register | 0x10 | 40139 | 40140 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN12 | Control Setpoint | Holding Register | 0x10 | 40152 | 40153 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN13 | Control Setpoint | Holding Register | 0x10 | 40165 | 40166 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN14 | Control Setpoint | Holding Register | 0x10 | 40178 | 40179 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN15 | Control Setpoint | Holding Register | 0x10 | 40191 | 40192 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN16 | Control Setpoint | Holding Register | 0x10 | 40204 | 40205 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN17 | Control Setpoint | Holding Register | 0x10 | 40217 | 40218 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN18 | Control Setpoint | Holding Register | 0x10 | 40230 | 40231 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN19 | Control Setpoint | Holding Register | 0x10 | 40243 | 40244 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN2 | Control Setpoint | Holding Register | 0x10 | 40022 | 40023 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN20 | Control Setpoint | Holding Register | 0x10 | 40256 | 40257 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN21 | Control Setpoint | Holding Register | 0x10 | 40269 | 40270 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN22 | Control Setpoint | Holding Register | 0x10 | 40282 | 40283 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN23 | Control Setpoint | Holding Register | 0x10 | 40295 | 40296 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN24 | Control Setpoint | Holding Register | 0x10 | 40308 | 40309 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN25 | Control Setpoint | Holding Register | 0x10 | 40321 | 40322 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN26 | Control Setpoint | Holding Register | 0x10 | 40334 | 40335 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN27 | Control Setpoint | Holding Register | 0x10 | 40347 | 40348 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN28 | Control Setpoint | Holding Register | 0x10 | 40360 | 40361 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN29 | Control Setpoint | Holding Register | 0x10 | 40373 | 40374 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN3 | Control Setpoint | Holding Register | 0x10 | 40035 | 40036 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN30 | Control Setpoint | Holding Register | 0x10 | 40386 | 40387 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN31 | Control Setpoint | Holding Register | 0x10 | 40399 | 40400 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN32 | Control Setpoint | Holding Register | 0x10 | 40412 | 40413 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN33 | Control Setpoint | Holding Register | 0x10 | 40425 | 40426 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN34 | Control Setpoint | Holding Register | 0x10 | 40438 | 40439 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN35 | Control Setpoint | Holding Register | 0x10 | 40451 | 40452 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN36 | Control Setpoint | Holding Register | 0x10 | 40464 | 40465 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN37 | Control Setpoint | Holding Register | 0x10 | 40477 | 40478 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN38 | Control Setpoint | Holding Register | 0x10 | 40490 | 40491 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN39 | Control Setpoint | Holding Register | 0x10 | 40503 | 40504 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN4 | Control Setpoint | Holding Register | 0x10 | 40048 | 40049 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN40 | Control Setpoint | Holding Register | 0x10 | 40516 | 40517 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN41 | Control Setpoint | Holding Register | 0x10 | 40529 | 40530 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN42 | Control Setpoint | Holding Register | 0x10 | 40542 | 40543 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN43 | Control Setpoint | Holding Register | 0x10 | 40555 | 40556 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN44 | Control Setpoint | Holding Register | 0x10 | 40568 | 40569 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN45 | Control Setpoint | Holding Register | 0x10 | 40581 | 40582 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN46 | Control Setpoint | Holding Register | 0x10 | 40594 | 40595 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN5 | Control Setpoint | Holding Register | 0x10 | 40061 | 40062 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN6 | Control Setpoint | Holding Register | 0x10 | 40074 | 40075 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN7 | Control Setpoint | Holding Register | 0x10 | 40087 | 40088 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN8 | Control Setpoint | Holding Register | 0x10 | 40100 | 40101 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_LowerRegLimit_SET | Yes | Operator defined MVAR lower regulation limit for GEN9 | Control Setpoint | Holding Register | 0x10 | 40113 | 40114 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G1 | Control Setpoint | Holding Register | 0x10 | 40007 | 40008 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G10 | Control Setpoint | Holding Register | 0x10 | 40124 | 40125 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G11 | Control Setpoint | Holding Register | 0x10 | 40137 | 40138 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G12 | Control Setpoint | Holding Register | 0x10 | 40150 | 40151 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G13 | Control Setpoint | Holding Register | 0x10 | 40163 | 40164 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G14 | Control Setpoint | Holding Register | 0x10 | 40176 | 40177 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G15 | Control Setpoint | Holding Register | 0x10 | 40189 | 40190 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G16 | Control Setpoint | Holding Register | 0x10 | 40202 | 40203 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G17 | Control Setpoint | Holding Register | 0x10 | 40215 | 40216 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G18 | Control Setpoint | Holding Register | 0x10 | 40228 | 40229 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G19 | Control Setpoint | Holding Register | 0x10 | 40241 | 40242 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G2 | Control Setpoint | Holding Register | 0x10 | 40020 | 40021 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G20 | Control Setpoint | Holding Register | 0x10 | 40254 | 40255 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G21 | Control Setpoint | Holding Register | 0x10 | 40267 | 40268 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G22 | Control Setpoint | Holding Register | 0x10 | 40280 | 40281 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G23 | Control Setpoint | Holding Register | 0x10 | 40293 | 40294 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G24 | Control Setpoint | Holding Register | 0x10 | 40306 | 40307 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G25 | Control Setpoint | Holding Register | 0x10 | 40319 | 40320 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G26 | Control Setpoint | Holding Register | 0x10 | 40332 | 40333 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G27 | Control Setpoint | Holding Register | 0x10 | 40345 | 40346 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G28 | Control Setpoint | Holding Register | 0x10 | 40358 | 40359 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G29 | Control Setpoint | Holding Register | 0x10 | 40371 | 40372 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G3 | Control Setpoint | Holding Register | 0x10 | 40033 | 40034 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G30 | Control Setpoint | Holding Register | 0x10 | 40384 | 40385 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G31 | Control Setpoint | Holding Register | 0x10 | 40397 | 40398 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G32 | Control Setpoint | Holding Register | 0x10 | 40410 | 40411 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G33 | Control Setpoint | Holding Register | 0x10 | 40423 | 40424 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G34 | Control Setpoint | Holding Register | 0x10 | 40436 | 40437 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G35 | Control Setpoint | Holding Register | 0x10 | 40449 | 40450 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G36 | Control Setpoint | Holding Register | 0x10 | 40462 | 40463 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G37 | Control Setpoint | Holding Register | 0x10 | 40475 | 40476 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G38 | Control Setpoint | Holding Register | 0x10 | 40488 | 40489 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G39 | Control Setpoint | Holding Register | 0x10 | 40501 | 40502 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G4 | Control Setpoint | Holding Register | 0x10 | 40046 | 40047 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G40 | Control Setpoint | Holding Register | 0x10 | 40514 | 40515 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G41 | Control Setpoint | Holding Register | 0x10 | 40527 | 40528 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G42 | Control Setpoint | Holding Register | 0x10 | 40540 | 40541 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G43 | Control Setpoint | Holding Register | 0x10 | 40553 | 40554 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G44 | Control Setpoint | Holding Register | 0x10 | 40566 | 40567 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G45 | Control Setpoint | Holding Register | 0x10 | 40579 | 40580 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G46 | Control Setpoint | Holding Register | 0x10 | 40592 | 40593 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G5 | Control Setpoint | Holding Register | 0x10 | 40059 | 40060 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G6 | Control Setpoint | Holding Register | 0x10 | 40072 | 40073 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G7 | Control Setpoint | Holding Register | 0x10 | 40085 | 40086 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G8 | Control Setpoint | Holding Register | 0x10 | 40098 | 40099 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_BaseSetpoint_SET | Yes | Operator defined MVAR Manual setpoint for G9 | Control Setpoint | Holding Register | 0x10 | 40111 | 40112 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN1 | Control Setpoint | Holding Register | 0x10 | 40011 | 40012 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN10 | Control Setpoint | Holding Register | 0x10 | 40128 | 40129 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN11 | Control Setpoint | Holding Register | 0x10 | 40141 | 40142 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN12 | Control Setpoint | Holding Register | 0x10 | 40154 | 40155 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN13 | Control Setpoint | Holding Register | 0x10 | 40167 | 40168 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN14 | Control Setpoint | Holding Register | 0x10 | 40180 | 40181 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN15 | Control Setpoint | Holding Register | 0x10 | 40193 | 40194 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN16 | Control Setpoint | Holding Register | 0x10 | 40206 | 40207 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN17 | Control Setpoint | Holding Register | 0x10 | 40219 | 40220 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN18 | Control Setpoint | Holding Register | 0x10 | 40232 | 40233 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN19 | Control Setpoint | Holding Register | 0x10 | 40245 | 40246 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN2 | Control Setpoint | Holding Register | 0x10 | 40024 | 40025 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN20 | Control Setpoint | Holding Register | 0x10 | 40258 | 40259 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN21 | Control Setpoint | Holding Register | 0x10 | 40271 | 40272 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN22 | Control Setpoint | Holding Register | 0x10 | 40284 | 40285 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN23 | Control Setpoint | Holding Register | 0x10 | 40297 | 40298 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN24 | Control Setpoint | Holding Register | 0x10 | 40310 | 40311 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN25 | Control Setpoint | Holding Register | 0x10 | 40323 | 40324 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN26 | Control Setpoint | Holding Register | 0x10 | 40336 | 40337 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN27 | Control Setpoint | Holding Register | 0x10 | 40349 | 40350 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN28 | Control Setpoint | Holding Register | 0x10 | 40362 | 40363 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN29 | Control Setpoint | Holding Register | 0x10 | 40375 | 40376 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN3 | Control Setpoint | Holding Register | 0x10 | 40037 | 40038 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN30 | Control Setpoint | Holding Register | 0x10 | 40388 | 40389 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN31 | Control Setpoint | Holding Register | 0x10 | 40401 | 40402 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN32 | Control Setpoint | Holding Register | 0x10 | 40414 | 40415 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN33 | Control Setpoint | Holding Register | 0x10 | 40427 | 40428 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN34 | Control Setpoint | Holding Register | 0x10 | 40440 | 40441 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN35 | Control Setpoint | Holding Register | 0x10 | 40453 | 40454 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN36 | Control Setpoint | Holding Register | 0x10 | 40466 | 40467 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN37 | Control Setpoint | Holding Register | 0x10 | 40479 | 40480 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN38 | Control Setpoint | Holding Register | 0x10 | 40492 | 40493 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN39 | Control Setpoint | Holding Register | 0x10 | 40505 | 40506 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN4 | Control Setpoint | Holding Register | 0x10 | 40050 | 40051 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN40 | Control Setpoint | Holding Register | 0x10 | 40518 | 40519 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN41 | Control Setpoint | Holding Register | 0x10 | 40531 | 40532 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN42 | Control Setpoint | Holding Register | 0x10 | 40544 | 40545 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN43 | Control Setpoint | Holding Register | 0x10 | 40557 | 40558 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN44 | Control Setpoint | Holding Register | 0x10 | 40570 | 40571 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN45 | Control Setpoint | Holding Register | 0x10 | 40583 | 40584 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN46 | Control Setpoint | Holding Register | 0x10 | 40596 | 40597 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN5 | Control Setpoint | Holding Register | 0x10 | 40063 | 40064 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN6 | Control Setpoint | Holding Register | 0x10 | 40076 | 40077 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN7 | Control Setpoint | Holding Register | 0x10 | 40089 | 40090 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN8 | Control Setpoint | Holding Register | 0x10 | 40102 | 40103 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_UpperRegLimit_SET | Yes | Operator defined MVAR upper regulation limit setpoint for GEN9 | Control Setpoint | Holding Register | 0x10 | 40115 | 40116 | 2 | Float | Yes | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN1 | Control Setpoint | Holding Register | 0x10 | 40003 | 40004 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN10 | Control Setpoint | Holding Register | 0x10 | 40120 | 40121 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN11 | Control Setpoint | Holding Register | 0x10 | 40133 | 40134 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN12 | Control Setpoint | Holding Register | 0x10 | 40146 | 40147 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN13 | Control Setpoint | Holding Register | 0x10 | 40159 | 40160 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN14 | Control Setpoint | Holding Register | 0x10 | 40172 | 40173 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN15 | Control Setpoint | Holding Register | 0x10 | 40185 | 40186 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN16 | Control Setpoint | Holding Register | 0x10 | 40198 | 40199 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN17 | Control Setpoint | Holding Register | 0x10 | 40211 | 40212 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN18 | Control Setpoint | Holding Register | 0x10 | 40224 | 40225 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN19 | Control Setpoint | Holding Register | 0x10 | 40237 | 40238 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN2 | Control Setpoint | Holding Register | 0x10 | 40016 | 40017 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN20 | Control Setpoint | Holding Register | 0x10 | 40250 | 40251 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN21 | Control Setpoint | Holding Register | 0x10 | 40263 | 40264 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN22 | Control Setpoint | Holding Register | 0x10 | 40276 | 40277 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN23 | Control Setpoint | Holding Register | 0x10 | 40289 | 40290 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN24 | Control Setpoint | Holding Register | 0x10 | 40302 | 40303 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN25 | Control Setpoint | Holding Register | 0x10 | 40315 | 40316 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN26 | Control Setpoint | Holding Register | 0x10 | 40328 | 40329 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN27 | Control Setpoint | Holding Register | 0x10 | 40341 | 40342 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN28 | Control Setpoint | Holding Register | 0x10 | 40354 | 40355 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN29 | Control Setpoint | Holding Register | 0x10 | 40367 | 40368 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN3 | Control Setpoint | Holding Register | 0x10 | 40029 | 40030 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN30 | Control Setpoint | Holding Register | 0x10 | 40380 | 40381 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN31 | Control Setpoint | Holding Register | 0x10 | 40393 | 40394 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN32 | Control Setpoint | Holding Register | 0x10 | 40406 | 40407 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN33 | Control Setpoint | Holding Register | 0x10 | 40419 | 40420 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN34 | Control Setpoint | Holding Register | 0x10 | 40432 | 40433 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN35 | Control Setpoint | Holding Register | 0x10 | 40445 | 40446 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN36 | Control Setpoint | Holding Register | 0x10 | 40458 | 40459 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN37 | Control Setpoint | Holding Register | 0x10 | 40471 | 40472 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN38 | Control Setpoint | Holding Register | 0x10 | 40484 | 40485 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN39 | Control Setpoint | Holding Register | 0x10 | 40497 | 40498 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN4 | Control Setpoint | Holding Register | 0x10 | 40042 | 40043 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN40 | Control Setpoint | Holding Register | 0x10 | 40510 | 40511 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN41 | Control Setpoint | Holding Register | 0x10 | 40523 | 40524 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN42 | Control Setpoint | Holding Register | 0x10 | 40536 | 40537 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN43 | Control Setpoint | Holding Register | 0x10 | 40549 | 40550 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN44 | Control Setpoint | Holding Register | 0x10 | 40562 | 40563 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN45 | Control Setpoint | Holding Register | 0x10 | 40575 | 40576 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN46 | Control Setpoint | Holding Register | 0x10 | 40588 | 40589 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN5 | Control Setpoint | Holding Register | 0x10 | 40055 | 40056 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN6 | Control Setpoint | Holding Register | 0x10 | 40068 | 40069 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN7 | Control Setpoint | Holding Register | 0x10 | 40081 | 40082 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN8 | Control Setpoint | Holding Register | 0x10 | 40094 | 40095 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_LowerRegLimit_SET | Yes | Operator defined MW lower regulation limit for GEN9 | Control Setpoint | Holding Register | 0x10 | 40107 | 40108 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G1 | Control Setpoint | Holding Register | 0x10 | 40001 | 40002 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G10 | Control Setpoint | Holding Register | 0x10 | 40118 | 40119 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G11 | Control Setpoint | Holding Register | 0x10 | 40131 | 40132 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G12 | Control Setpoint | Holding Register | 0x10 | 40144 | 40145 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G13 | Control Setpoint | Holding Register | 0x10 | 40157 | 40158 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G14 | Control Setpoint | Holding Register | 0x10 | 40170 | 40171 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G15 | Control Setpoint | Holding Register | 0x10 | 40183 | 40184 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G16 | Control Setpoint | Holding Register | 0x10 | 40196 | 40197 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G17 | Control Setpoint | Holding Register | 0x10 | 40209 | 40210 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G18 | Control Setpoint | Holding Register | 0x10 | 40222 | 40223 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G19 | Control Setpoint | Holding Register | 0x10 | 40235 | 40236 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G2 | Control Setpoint | Holding Register | 0x10 | 40014 | 40015 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G20 | Control Setpoint | Holding Register | 0x10 | 40248 | 40249 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G21 | Control Setpoint | Holding Register | 0x10 | 40261 | 40262 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G22 | Control Setpoint | Holding Register | 0x10 | 40274 | 40275 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G23 | Control Setpoint | Holding Register | 0x10 | 40287 | 40288 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G24 | Control Setpoint | Holding Register | 0x10 | 40300 | 40301 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G25 | Control Setpoint | Holding Register | 0x10 | 40313 | 40314 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G26 | Control Setpoint | Holding Register | 0x10 | 40326 | 40327 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G27 | Control Setpoint | Holding Register | 0x10 | 40339 | 40340 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G28 | Control Setpoint | Holding Register | 0x10 | 40352 | 40353 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G29 | Control Setpoint | Holding Register | 0x10 | 40365 | 40366 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G3 | Control Setpoint | Holding Register | 0x10 | 40027 | 40028 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G30 | Control Setpoint | Holding Register | 0x10 | 40378 | 40379 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G31 | Control Setpoint | Holding Register | 0x10 | 40391 | 40392 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G32 | Control Setpoint | Holding Register | 0x10 | 40404 | 40405 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G33 | Control Setpoint | Holding Register | 0x10 | 40417 | 40418 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G34 | Control Setpoint | Holding Register | 0x10 | 40430 | 40431 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G35 | Control Setpoint | Holding Register | 0x10 | 40443 | 40444 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G36 | Control Setpoint | Holding Register | 0x10 | 40456 | 40457 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G37 | Control Setpoint | Holding Register | 0x10 | 40469 | 40470 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G38 | Control Setpoint | Holding Register | 0x10 | 40482 | 40483 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G39 | Control Setpoint | Holding Register | 0x10 | 40495 | 40496 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G4 | Control Setpoint | Holding Register | 0x10 | 40040 | 40041 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G40 | Control Setpoint | Holding Register | 0x10 | 40508 | 40509 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G41 | Control Setpoint | Holding Register | 0x10 | 40521 | 40522 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G42 | Control Setpoint | Holding Register | 0x10 | 40534 | 40535 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G43 | Control Setpoint | Holding Register | 0x10 | 40547 | 40548 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G44 | Control Setpoint | Holding Register | 0x10 | 40560 | 40561 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G45 | Control Setpoint | Holding Register | 0x10 | 40573 | 40574 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G46 | Control Setpoint | Holding Register | 0x10 | 40586 | 40587 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G5 | Control Setpoint | Holding Register | 0x10 | 40053 | 40054 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G6 | Control Setpoint | Holding Register | 0x10 | 40066 | 40067 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G7 | Control Setpoint | Holding Register | 0x10 | 40079 | 40080 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G8 | Control Setpoint | Holding Register | 0x10 | 40092 | 40093 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_BaseSetpoint_SET | Yes | Operator defined MW Manual setpoint for G9 | Control Setpoint | Holding Register | 0x10 | 40105 | 40106 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN1 | Control Setpoint | Holding Register | 0x10 | 40005 | 40006 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN10 | Control Setpoint | Holding Register | 0x10 | 40122 | 40123 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN11 | Control Setpoint | Holding Register | 0x10 | 40135 | 40136 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN12 | Control Setpoint | Holding Register | 0x10 | 40148 | 40149 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN13 | Control Setpoint | Holding Register | 0x10 | 40161 | 40162 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN14 | Control Setpoint | Holding Register | 0x10 | 40174 | 40175 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN15 | Control Setpoint | Holding Register | 0x10 | 40187 | 40188 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN16 | Control Setpoint | Holding Register | 0x10 | 40200 | 40201 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN17 | Control Setpoint | Holding Register | 0x10 | 40213 | 40214 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN18 | Control Setpoint | Holding Register | 0x10 | 40226 | 40227 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN19 | Control Setpoint | Holding Register | 0x10 | 40239 | 40240 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN2 | Control Setpoint | Holding Register | 0x10 | 40018 | 40019 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN20 | Control Setpoint | Holding Register | 0x10 | 40252 | 40253 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN21 | Control Setpoint | Holding Register | 0x10 | 40265 | 40266 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN22 | Control Setpoint | Holding Register | 0x10 | 40278 | 40279 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN23 | Control Setpoint | Holding Register | 0x10 | 40291 | 40292 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN24 | Control Setpoint | Holding Register | 0x10 | 40304 | 40305 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN25 | Control Setpoint | Holding Register | 0x10 | 40317 | 40318 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN26 | Control Setpoint | Holding Register | 0x10 | 40330 | 40331 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN27 | Control Setpoint | Holding Register | 0x10 | 40343 | 40344 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN28 | Control Setpoint | Holding Register | 0x10 | 40356 | 40357 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN29 | Control Setpoint | Holding Register | 0x10 | 40369 | 40370 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN3 | Control Setpoint | Holding Register | 0x10 | 40031 | 40032 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN30 | Control Setpoint | Holding Register | 0x10 | 40382 | 40383 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN31 | Control Setpoint | Holding Register | 0x10 | 40395 | 40396 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN32 | Control Setpoint | Holding Register | 0x10 | 40408 | 40409 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN33 | Control Setpoint | Holding Register | 0x10 | 40421 | 40422 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN34 | Control Setpoint | Holding Register | 0x10 | 40434 | 40435 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN35 | Control Setpoint | Holding Register | 0x10 | 40447 | 40448 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN36 | Control Setpoint | Holding Register | 0x10 | 40460 | 40461 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN37 | Control Setpoint | Holding Register | 0x10 | 40473 | 40474 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN38 | Control Setpoint | Holding Register | 0x10 | 40486 | 40487 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN39 | Control Setpoint | Holding Register | 0x10 | 40499 | 40500 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN4 | Control Setpoint | Holding Register | 0x10 | 40044 | 40045 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN40 | Control Setpoint | Holding Register | 0x10 | 40512 | 40513 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN41 | Control Setpoint | Holding Register | 0x10 | 40525 | 40526 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN42 | Control Setpoint | Holding Register | 0x10 | 40538 | 40539 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN43 | Control Setpoint | Holding Register | 0x10 | 40551 | 40552 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN44 | Control Setpoint | Holding Register | 0x10 | 40564 | 40565 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN45 | Control Setpoint | Holding Register | 0x10 | 40577 | 40578 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN46 | Control Setpoint | Holding Register | 0x10 | 40590 | 40591 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN5 | Control Setpoint | Holding Register | 0x10 | 40057 | 40058 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN6 | Control Setpoint | Holding Register | 0x10 | 40070 | 40071 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN7 | Control Setpoint | Holding Register | 0x10 | 40083 | 40084 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN8 | Control Setpoint | Holding Register | 0x10 | 40096 | 40097 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_UpperRegLimit_SET | Yes | Operator defined MW upper regulation limit setpoint for GEN9 | Control Setpoint | Holding Register | 0x10 | 40109 | 40110 | 2 | Float | Yes | 32 bit float MSR | MW | 1 Unit = 1 MW
Generation Management Control Screens | N/A | N/A | GMS_PartyModeDisable_CMD | Yes | Operator disable command for AI load fluctuation mode (pulse) | Command | Coil | 0x05 | 570 | 570 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | N/A | N/A | GMS_MLMEnable_CMD | Yes | Operator enable/disable command for minimum load management | Command | Coil | 0x05 | 571 | 571 | 1 | Boolean | Yes | N/A | Latch | 0=disabled, 1=enabled
Generation Management Control Screens | N/A | N/A | GMS_PartyModeEnable_CMD | Yes | Operator input to start party mode manually | Command | Coil | 0x05 | 379 | 379 | 1 | Boolean | Yes | N/A | Latch | 0=disable, 1=enable
Blackstart Sequence | N/A | N/A | BS_InitiateBlackstart_CMD | Yes | Operator manual initiate blackstart sequence | Command | Coil | 0x05 | 373 | 373 | 1 | Boolean | Yes | N/A | Pulse | N/A
Blackstart Sequence | N/A | N/A | BS_RecoveryManualRearm_CMD | Yes | Operator manual re-arm command for blackout recovery sequence | Command | Coil | 0x05 | 374 | 374 | 1 | Boolean | Yes | N/A | Pulse | N/A
Voltage Control System Screens | SYNCON | N/A | SC_GenPFObj_VAL | Yes | Operator setpoint for PF objective available on Syn-Con popup |  | Input Register | 0x04 | 2986 | 2987 | 2 | Float | No | 32 bit float MSR | N/A | N/A
Generation Management Control Screens | N/A | N/A | GMS_PartyModeEnabled_STAT | Yes | Party mode active status feedback |  | Discrete Input | 0x02 | 11050 | 11050 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN1 | Operation Message | Discrete Input | 0x02 | 11059 | 11059 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN10 | Operation Message | Discrete Input | 0x02 | 11068 | 11068 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN11 | Operation Message | Discrete Input | 0x02 | 11069 | 11069 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN12 | Operation Message | Discrete Input | 0x02 | 11070 | 11070 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN13 | Operation Message | Discrete Input | 0x02 | 11071 | 11071 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN14 | Operation Message | Discrete Input | 0x02 | 11072 | 11072 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN15 | Operation Message | Discrete Input | 0x02 | 11073 | 11073 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN16 | Operation Message | Discrete Input | 0x02 | 11074 | 11074 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN17 | Operation Message | Discrete Input | 0x02 | 11075 | 11075 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN18 | Operation Message | Discrete Input | 0x02 | 11076 | 11076 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN19 | Operation Message | Discrete Input | 0x02 | 11077 | 11077 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN2 | Operation Message | Discrete Input | 0x02 | 11060 | 11060 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN20 | Operation Message | Discrete Input | 0x02 | 11078 | 11078 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN21 | Operation Message | Discrete Input | 0x02 | 11079 | 11079 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN22 | Operation Message | Discrete Input | 0x02 | 11080 | 11080 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN23 | Operation Message | Discrete Input | 0x02 | 11081 | 11081 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN24 | Operation Message | Discrete Input | 0x02 | 11082 | 11082 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN25 | Operation Message | Discrete Input | 0x02 | 11083 | 11083 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN26 | Operation Message | Discrete Input | 0x02 | 11084 | 11084 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN27 | Operation Message | Discrete Input | 0x02 | 11085 | 11085 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN28 | Operation Message | Discrete Input | 0x02 | 11086 | 11086 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN29 | Operation Message | Discrete Input | 0x02 | 11087 | 11087 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN3 | Operation Message | Discrete Input | 0x02 | 11061 | 11061 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN30 | Operation Message | Discrete Input | 0x02 | 11088 | 11088 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN31 | Operation Message | Discrete Input | 0x02 | 11089 | 11089 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN32 | Operation Message | Discrete Input | 0x02 | 11090 | 11090 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN33 | Operation Message | Discrete Input | 0x02 | 11091 | 11091 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN34 | Operation Message | Discrete Input | 0x02 | 11092 | 11092 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN35 | Operation Message | Discrete Input | 0x02 | 11093 | 11093 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN36 | Operation Message | Discrete Input | 0x02 | 11094 | 11094 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN37 | Operation Message | Discrete Input | 0x02 | 11095 | 11095 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN38 | Operation Message | Discrete Input | 0x02 | 11096 | 11096 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN39 | Operation Message | Discrete Input | 0x02 | 11097 | 11097 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN4 | Operation Message | Discrete Input | 0x02 | 11062 | 11062 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN40 | Operation Message | Discrete Input | 0x02 | 11098 | 11098 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN41 | Operation Message | Discrete Input | 0x02 | 11099 | 11099 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN42 | Operation Message | Discrete Input | 0x02 | 11100 | 11100 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN43 | Operation Message | Discrete Input | 0x02 | 11101 | 11101 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN44 | Operation Message | Discrete Input | 0x02 | 11102 | 11102 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN45 | Operation Message | Discrete Input | 0x02 | 11103 | 11103 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN46 | Operation Message | Discrete Input | 0x02 | 11104 | 11104 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN5 | Operation Message | Discrete Input | 0x02 | 11063 | 11063 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN6 | Operation Message | Discrete Input | 0x02 | 11064 | 11064 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN7 | Operation Message | Discrete Input | 0x02 | 11065 | 11065 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN8 | Operation Message | Discrete Input | 0x02 | 11066 | 11066 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_AutoManual_STAT | Yes | PowerMAX Controller Auto/Manual control mode status for GEN9 | Operation Message | Discrete Input | 0x02 | 11067 | 11067 | 1 | Boolean | No | N/A | Latch | 0=manual, 1=auto
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN1 | Operation Message | Discrete Input | 0x02 | 10007 | 10007 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN1 | Operation Message | Discrete Input | 0x02 | 10018 | 10018 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN10 | Operation Message | Discrete Input | 0x02 | 10196 | 10196 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN10 | Operation Message | Discrete Input | 0x02 | 10207 | 10207 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN11 | Operation Message | Discrete Input | 0x02 | 10217 | 10217 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN11 | Operation Message | Discrete Input | 0x02 | 10228 | 10228 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN12 | Operation Message | Discrete Input | 0x02 | 10238 | 10238 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN12 | Operation Message | Discrete Input | 0x02 | 10249 | 10249 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN13 | Operation Message | Discrete Input | 0x02 | 10259 | 10259 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN13 | Operation Message | Discrete Input | 0x02 | 10270 | 10270 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN14 | Operation Message | Discrete Input | 0x02 | 10280 | 10280 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN14 | Operation Message | Discrete Input | 0x02 | 10291 | 10291 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN15 | Operation Message | Discrete Input | 0x02 | 10301 | 10301 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN15 | Operation Message | Discrete Input | 0x02 | 10312 | 10312 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN16 | Operation Message | Discrete Input | 0x02 | 10322 | 10322 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN16 | Operation Message | Discrete Input | 0x02 | 10333 | 10333 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN17 | Operation Message | Discrete Input | 0x02 | 10343 | 10343 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN17 | Operation Message | Discrete Input | 0x02 | 10354 | 10354 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN18 | Operation Message | Discrete Input | 0x02 | 10364 | 10364 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN18 | Operation Message | Discrete Input | 0x02 | 10375 | 10375 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN19 | Operation Message | Discrete Input | 0x02 | 10385 | 10385 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN19 | Operation Message | Discrete Input | 0x02 | 10396 | 10396 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN2 | Operation Message | Discrete Input | 0x02 | 10028 | 10028 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN2 | Operation Message | Discrete Input | 0x02 | 10039 | 10039 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN20 | Operation Message | Discrete Input | 0x02 | 10406 | 10406 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN20 | Operation Message | Discrete Input | 0x02 | 10417 | 10417 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN21 | Operation Message | Discrete Input | 0x02 | 10427 | 10427 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN21 | Operation Message | Discrete Input | 0x02 | 10438 | 10438 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN22 | Operation Message | Discrete Input | 0x02 | 10448 | 10448 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN22 | Operation Message | Discrete Input | 0x02 | 10459 | 10459 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN23 | Operation Message | Discrete Input | 0x02 | 10469 | 10469 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN23 | Operation Message | Discrete Input | 0x02 | 10480 | 10480 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN24 | Operation Message | Discrete Input | 0x02 | 10490 | 10490 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN24 | Operation Message | Discrete Input | 0x02 | 10501 | 10501 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN25 | Operation Message | Discrete Input | 0x02 | 10511 | 10511 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN25 | Operation Message | Discrete Input | 0x02 | 10522 | 10522 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN26 | Operation Message | Discrete Input | 0x02 | 10532 | 10532 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN26 | Operation Message | Discrete Input | 0x02 | 10543 | 10543 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN27 | Operation Message | Discrete Input | 0x02 | 10553 | 10553 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN27 | Operation Message | Discrete Input | 0x02 | 10564 | 10564 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN28 | Operation Message | Discrete Input | 0x02 | 10574 | 10574 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN28 | Operation Message | Discrete Input | 0x02 | 10585 | 10585 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN29 | Operation Message | Discrete Input | 0x02 | 10595 | 10595 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN29 | Operation Message | Discrete Input | 0x02 | 10606 | 10606 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN3 | Operation Message | Discrete Input | 0x02 | 10049 | 10049 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN3 | Operation Message | Discrete Input | 0x02 | 10060 | 10060 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN30 | Operation Message | Discrete Input | 0x02 | 10616 | 10616 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN30 | Operation Message | Discrete Input | 0x02 | 10627 | 10627 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN31 | Operation Message | Discrete Input | 0x02 | 10637 | 10637 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN31 | Operation Message | Discrete Input | 0x02 | 10648 | 10648 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN32 | Operation Message | Discrete Input | 0x02 | 10658 | 10658 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN32 | Operation Message | Discrete Input | 0x02 | 10669 | 10669 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN33 | Operation Message | Discrete Input | 0x02 | 10679 | 10679 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN33 | Operation Message | Discrete Input | 0x02 | 10690 | 10690 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN34 | Operation Message | Discrete Input | 0x02 | 10700 | 10700 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN34 | Operation Message | Discrete Input | 0x02 | 10711 | 10711 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN35 | Operation Message | Discrete Input | 0x02 | 10721 | 10721 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN35 | Operation Message | Discrete Input | 0x02 | 10732 | 10732 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN36 | Operation Message | Discrete Input | 0x02 | 10742 | 10742 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN36 | Operation Message | Discrete Input | 0x02 | 10753 | 10753 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN37 | Operation Message | Discrete Input | 0x02 | 10763 | 10763 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN37 | Operation Message | Discrete Input | 0x02 | 10774 | 10774 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN38 | Operation Message | Discrete Input | 0x02 | 10784 | 10784 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN38 | Operation Message | Discrete Input | 0x02 | 10795 | 10795 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN39 | Operation Message | Discrete Input | 0x02 | 10805 | 10805 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN39 | Operation Message | Discrete Input | 0x02 | 10816 | 10816 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN4 | Operation Message | Discrete Input | 0x02 | 10070 | 10070 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN4 | Operation Message | Discrete Input | 0x02 | 10081 | 10081 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN40 | Operation Message | Discrete Input | 0x02 | 10826 | 10826 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN40 | Operation Message | Discrete Input | 0x02 | 10837 | 10837 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN41 | Operation Message | Discrete Input | 0x02 | 10847 | 10847 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN41 | Operation Message | Discrete Input | 0x02 | 10858 | 10858 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN42 | Operation Message | Discrete Input | 0x02 | 10868 | 10868 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN42 | Operation Message | Discrete Input | 0x02 | 10879 | 10879 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN43 | Operation Message | Discrete Input | 0x02 | 10889 | 10889 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN43 | Operation Message | Discrete Input | 0x02 | 10900 | 10900 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN44 | Operation Message | Discrete Input | 0x02 | 10910 | 10910 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN44 | Operation Message | Discrete Input | 0x02 | 10921 | 10921 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN45 | Operation Message | Discrete Input | 0x02 | 10931 | 10931 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN45 | Operation Message | Discrete Input | 0x02 | 10942 | 10942 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN46 | Operation Message | Discrete Input | 0x02 | 10952 | 10952 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN46 | Operation Message | Discrete Input | 0x02 | 10963 | 10963 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN5 | Operation Message | Discrete Input | 0x02 | 10091 | 10091 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN5 | Operation Message | Discrete Input | 0x02 | 10102 | 10102 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN6 | Operation Message | Discrete Input | 0x02 | 10112 | 10112 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN6 | Operation Message | Discrete Input | 0x02 | 10123 | 10123 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN7 | Operation Message | Discrete Input | 0x02 | 10133 | 10133 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN7 | Operation Message | Discrete Input | 0x02 | 10144 | 10144 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN8 | Operation Message | Discrete Input | 0x02 | 10154 | 10154 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN8 | Operation Message | Discrete Input | 0x02 | 10165 | 10165 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN9 | Operation Message | Discrete Input | 0x02 | 10175 | 10175 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_ControlPermissive_STAT | Yes | PowerMAX Controller control permissive - GEN9 | Operation Message | Discrete Input | 0x02 | 10186 | 10186 | 1 | Boolean | No | N/A | Latch | 1 = Under PMS Control, 0 = Not under PMS Control
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN1 | Operation Message | Discrete Input | 0x02 | 10014 | 10014 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN10 | Operation Message | Discrete Input | 0x02 | 10203 | 10203 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN11 | Operation Message | Discrete Input | 0x02 | 10224 | 10224 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN12 | Operation Message | Discrete Input | 0x02 | 10245 | 10245 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN13 | Operation Message | Discrete Input | 0x02 | 10266 | 10266 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN14 | Operation Message | Discrete Input | 0x02 | 10287 | 10287 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN15 | Operation Message | Discrete Input | 0x02 | 10308 | 10308 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN16 | Operation Message | Discrete Input | 0x02 | 10329 | 10329 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN17 | Operation Message | Discrete Input | 0x02 | 10350 | 10350 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN18 | Operation Message | Discrete Input | 0x02 | 10371 | 10371 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN19 | Operation Message | Discrete Input | 0x02 | 10392 | 10392 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN2 | Operation Message | Discrete Input | 0x02 | 10035 | 10035 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN20 | Operation Message | Discrete Input | 0x02 | 10413 | 10413 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN21 | Operation Message | Discrete Input | 0x02 | 10434 | 10434 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN22 | Operation Message | Discrete Input | 0x02 | 10455 | 10455 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN23 | Operation Message | Discrete Input | 0x02 | 10476 | 10476 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN24 | Operation Message | Discrete Input | 0x02 | 10497 | 10497 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN25 | Operation Message | Discrete Input | 0x02 | 10518 | 10518 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN26 | Operation Message | Discrete Input | 0x02 | 10539 | 10539 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN27 | Operation Message | Discrete Input | 0x02 | 10560 | 10560 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN28 | Operation Message | Discrete Input | 0x02 | 10581 | 10581 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN29 | Operation Message | Discrete Input | 0x02 | 10602 | 10602 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN3 | Operation Message | Discrete Input | 0x02 | 10056 | 10056 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN30 | Operation Message | Discrete Input | 0x02 | 10623 | 10623 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN31 | Operation Message | Discrete Input | 0x02 | 10644 | 10644 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN32 | Operation Message | Discrete Input | 0x02 | 10665 | 10665 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN33 | Operation Message | Discrete Input | 0x02 | 10686 | 10686 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN34 | Operation Message | Discrete Input | 0x02 | 10707 | 10707 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN35 | Operation Message | Discrete Input | 0x02 | 10728 | 10728 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN36 | Operation Message | Discrete Input | 0x02 | 10749 | 10749 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN37 | Operation Message | Discrete Input | 0x02 | 10770 | 10770 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN38 | Operation Message | Discrete Input | 0x02 | 10791 | 10791 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN39 | Operation Message | Discrete Input | 0x02 | 10812 | 10812 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN4 | Operation Message | Discrete Input | 0x02 | 10077 | 10077 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN40 | Operation Message | Discrete Input | 0x02 | 10833 | 10833 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN41 | Operation Message | Discrete Input | 0x02 | 10854 | 10854 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN42 | Operation Message | Discrete Input | 0x02 | 10875 | 10875 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN43 | Operation Message | Discrete Input | 0x02 | 10896 | 10896 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN44 | Operation Message | Discrete Input | 0x02 | 10917 | 10917 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN45 | Operation Message | Discrete Input | 0x02 | 10938 | 10938 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN46 | Operation Message | Discrete Input | 0x02 | 10959 | 10959 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN5 | Operation Message | Discrete Input | 0x02 | 10098 | 10098 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN6 | Operation Message | Discrete Input | 0x02 | 10119 | 10119 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN7 | Operation Message | Discrete Input | 0x02 | 10140 | 10140 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN8 | Operation Message | Discrete Input | 0x02 | 10161 | 10161 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_ControlInProgress_STAT | Yes | PowerMAX MVAR control in progress for GEN9 | Operation Message | Discrete Input | 0x02 | 10182 | 10182 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN1 | Operation Message | Discrete Input | 0x02 | 10003 | 10003 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN10 | Operation Message | Discrete Input | 0x02 | 10192 | 10192 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN11 | Operation Message | Discrete Input | 0x02 | 10213 | 10213 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN12 | Operation Message | Discrete Input | 0x02 | 10234 | 10234 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN13 | Operation Message | Discrete Input | 0x02 | 10255 | 10255 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN14 | Operation Message | Discrete Input | 0x02 | 10276 | 10276 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN15 | Operation Message | Discrete Input | 0x02 | 10297 | 10297 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN16 | Operation Message | Discrete Input | 0x02 | 10318 | 10318 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN17 | Operation Message | Discrete Input | 0x02 | 10339 | 10339 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN18 | Operation Message | Discrete Input | 0x02 | 10360 | 10360 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN19 | Operation Message | Discrete Input | 0x02 | 10381 | 10381 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN2 | Operation Message | Discrete Input | 0x02 | 10024 | 10024 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN20 | Operation Message | Discrete Input | 0x02 | 10402 | 10402 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN21 | Operation Message | Discrete Input | 0x02 | 10423 | 10423 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN22 | Operation Message | Discrete Input | 0x02 | 10444 | 10444 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN23 | Operation Message | Discrete Input | 0x02 | 10465 | 10465 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN24 | Operation Message | Discrete Input | 0x02 | 10486 | 10486 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN25 | Operation Message | Discrete Input | 0x02 | 10507 | 10507 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN26 | Operation Message | Discrete Input | 0x02 | 10528 | 10528 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN27 | Operation Message | Discrete Input | 0x02 | 10549 | 10549 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN28 | Operation Message | Discrete Input | 0x02 | 10570 | 10570 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN29 | Operation Message | Discrete Input | 0x02 | 10591 | 10591 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN3 | Operation Message | Discrete Input | 0x02 | 10045 | 10045 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN30 | Operation Message | Discrete Input | 0x02 | 10612 | 10612 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN31 | Operation Message | Discrete Input | 0x02 | 10633 | 10633 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN32 | Operation Message | Discrete Input | 0x02 | 10654 | 10654 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN33 | Operation Message | Discrete Input | 0x02 | 10675 | 10675 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN34 | Operation Message | Discrete Input | 0x02 | 10696 | 10696 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN35 | Operation Message | Discrete Input | 0x02 | 10717 | 10717 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN36 | Operation Message | Discrete Input | 0x02 | 10738 | 10738 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN37 | Operation Message | Discrete Input | 0x02 | 10759 | 10759 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN38 | Operation Message | Discrete Input | 0x02 | 10780 | 10780 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN39 | Operation Message | Discrete Input | 0x02 | 10801 | 10801 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN4 | Operation Message | Discrete Input | 0x02 | 10066 | 10066 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN40 | Operation Message | Discrete Input | 0x02 | 10822 | 10822 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN41 | Operation Message | Discrete Input | 0x02 | 10843 | 10843 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN42 | Operation Message | Discrete Input | 0x02 | 10864 | 10864 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN43 | Operation Message | Discrete Input | 0x02 | 10885 | 10885 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN44 | Operation Message | Discrete Input | 0x02 | 10906 | 10906 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN45 | Operation Message | Discrete Input | 0x02 | 10927 | 10927 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN46 | Operation Message | Discrete Input | 0x02 | 10948 | 10948 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN5 | Operation Message | Discrete Input | 0x02 | 10087 | 10087 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN6 | Operation Message | Discrete Input | 0x02 | 10108 | 10108 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN7 | Operation Message | Discrete Input | 0x02 | 10129 | 10129 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN8 | Operation Message | Discrete Input | 0x02 | 10150 | 10150 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_ControlInProgress_STAT | Yes | PowerMAX MW control in progress for GEN9 | Operation Message | Discrete Input | 0x02 | 10171 | 10171 | 1 | Boolean | No | N/A | Latch | 0=no action, 1=control in progress
Generation Management Control Screens | N\A | N\A | GMS_NewPriority_SET | Yes | Prepared value of new GMS running priority to be assigned to a selected generator |  | Holding Register | 0x06 | 40619 | 40619 | 1 | Int | Yes | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | QPAC-1 | GEN1 | GMS_G1_AlarmReset_CMD | Yes | Reset control alarms for GEN1 | Command | Coil | 0x05 | 5 | 5 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN10 | GMS_G10_AlarmReset_CMD | Yes | Reset control alarms for GEN10 | Command | Coil | 0x05 | 77 | 77 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN11 | GMS_G11_AlarmReset_CMD | Yes | Reset control alarms for GEN11 | Command | Coil | 0x05 | 85 | 85 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN12 | GMS_G12_AlarmReset_CMD | Yes | Reset control alarms for GEN12 | Command | Coil | 0x05 | 93 | 93 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN13 | GMS_G13_AlarmReset_CMD | Yes | Reset control alarms for GEN13 | Command | Coil | 0x05 | 101 | 101 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN14 | GMS_G14_AlarmReset_CMD | Yes | Reset control alarms for GEN14 | Command | Coil | 0x05 | 109 | 109 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN15 | GMS_G15_AlarmReset_CMD | Yes | Reset control alarms for GEN15 | Command | Coil | 0x05 | 117 | 117 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-4 | GEN16 | GMS_G16_AlarmReset_CMD | Yes | Reset control alarms for GEN16 | Command | Coil | 0x05 | 125 | 125 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN17 | GMS_G17_AlarmReset_CMD | Yes | Reset control alarms for GEN17 | Command | Coil | 0x05 | 133 | 133 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN18 | GMS_G18_AlarmReset_CMD | Yes | Reset control alarms for GEN18 | Command | Coil | 0x05 | 141 | 141 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN19 | GMS_G19_AlarmReset_CMD | Yes | Reset control alarms for GEN19 | Command | Coil | 0x05 | 149 | 149 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN2 | GMS_G2_AlarmReset_CMD | Yes | Reset control alarms for GEN2 | Command | Coil | 0x05 | 13 | 13 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-5 | GEN20 | GMS_G20_AlarmReset_CMD | Yes | Reset control alarms for GEN20 | Command | Coil | 0x05 | 157 | 157 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN21 | GMS_G21_AlarmReset_CMD | Yes | Reset control alarms for GEN21 | Command | Coil | 0x05 | 165 | 165 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN22 | GMS_G22_AlarmReset_CMD | Yes | Reset control alarms for GEN22 | Command | Coil | 0x05 | 173 | 173 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN23 | GMS_G23_AlarmReset_CMD | Yes | Reset control alarms for GEN23 | Command | Coil | 0x05 | 181 | 181 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-6 | GEN24 | GMS_G24_AlarmReset_CMD | Yes | Reset control alarms for GEN24 | Command | Coil | 0x05 | 189 | 189 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN25 | GMS_G25_AlarmReset_CMD | Yes | Reset control alarms for GEN25 | Command | Coil | 0x05 | 197 | 197 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN26 | GMS_G26_AlarmReset_CMD | Yes | Reset control alarms for GEN26 | Command | Coil | 0x05 | 205 | 205 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN27 | GMS_G27_AlarmReset_CMD | Yes | Reset control alarms for GEN27 | Command | Coil | 0x05 | 213 | 213 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-7 | GEN28 | GMS_G28_AlarmReset_CMD | Yes | Reset control alarms for GEN28 | Command | Coil | 0x05 | 221 | 221 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN29 | GMS_G29_AlarmReset_CMD | Yes | Reset control alarms for GEN29 | Command | Coil | 0x05 | 229 | 229 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN3 | GMS_G3_AlarmReset_CMD | Yes | Reset control alarms for GEN3 | Command | Coil | 0x05 | 21 | 21 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN30 | GMS_G30_AlarmReset_CMD | Yes | Reset control alarms for GEN30 | Command | Coil | 0x05 | 237 | 237 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN31 | GMS_G31_AlarmReset_CMD | Yes | Reset control alarms for GEN31 | Command | Coil | 0x05 | 245 | 245 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-8 | GEN32 | GMS_G32_AlarmReset_CMD | Yes | Reset control alarms for GEN32 | Command | Coil | 0x05 | 253 | 253 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN33 | GMS_G33_AlarmReset_CMD | Yes | Reset control alarms for GEN33 | Command | Coil | 0x05 | 261 | 261 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN34 | GMS_G34_AlarmReset_CMD | Yes | Reset control alarms for GEN34 | Command | Coil | 0x05 | 269 | 269 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN35 | GMS_G35_AlarmReset_CMD | Yes | Reset control alarms for GEN35 | Command | Coil | 0x05 | 277 | 277 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-9 | GEN36 | GMS_G36_AlarmReset_CMD | Yes | Reset control alarms for GEN36 | Command | Coil | 0x05 | 285 | 285 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN37 | GMS_G37_AlarmReset_CMD | Yes | Reset control alarms for GEN37 | Command | Coil | 0x05 | 293 | 293 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN38 | GMS_G38_AlarmReset_CMD | Yes | Reset control alarms for GEN38 | Command | Coil | 0x05 | 301 | 301 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN39 | GMS_G39_AlarmReset_CMD | Yes | Reset control alarms for GEN39 | Command | Coil | 0x05 | 309 | 309 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-1 | GEN4 | GMS_G4_AlarmReset_CMD | Yes | Reset control alarms for GEN4 | Command | Coil | 0x05 | 29 | 29 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-10 | GEN40 | GMS_G40_AlarmReset_CMD | Yes | Reset control alarms for GEN40 | Command | Coil | 0x05 | 317 | 317 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN41 | GMS_G41_AlarmReset_CMD | Yes | Reset control alarms for GEN41 | Command | Coil | 0x05 | 325 | 325 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN42 | GMS_G42_AlarmReset_CMD | Yes | Reset control alarms for GEN42 | Command | Coil | 0x05 | 333 | 333 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN43 | GMS_G43_AlarmReset_CMD | Yes | Reset control alarms for GEN43 | Command | Coil | 0x05 | 341 | 341 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-11 | GEN44 | GMS_G44_AlarmReset_CMD | Yes | Reset control alarms for GEN44 | Command | Coil | 0x05 | 349 | 349 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GEN45 | GMS_G45_AlarmReset_CMD | Yes | Reset control alarms for GEN45 | Command | Coil | 0x05 | 357 | 357 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-12 | GEN46 | GMS_G46_AlarmReset_CMD | Yes | Reset control alarms for GEN46 | Command | Coil | 0x05 | 365 | 365 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN5 | GMS_G5_AlarmReset_CMD | Yes | Reset control alarms for GEN5 | Command | Coil | 0x05 | 37 | 37 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN6 | GMS_G6_AlarmReset_CMD | Yes | Reset control alarms for GEN6 | Command | Coil | 0x05 | 45 | 45 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN7 | GMS_G7_AlarmReset_CMD | Yes | Reset control alarms for GEN7 | Command | Coil | 0x05 | 53 | 53 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-2 | GEN8 | GMS_G8_AlarmReset_CMD | Yes | Reset control alarms for GEN8 | Command | Coil | 0x05 | 61 | 61 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | QPAC-3 | GEN9 | GMS_G9_AlarmReset_CMD | Yes | Reset control alarms for GEN9 | Command | Coil | 0x05 | 69 | 69 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | SC1 | SC1_ResetAlarms | Yes | Reset IED alarms command for synchronous condenser 1 | Command | Coil | 0x05 | 572 | 572 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | SC2 | SC2_ResetAlarms | Yes | Reset IED alarms command for synchronous condenser 2 | Command | Coil | 0x05 | 573 | 573 | 1 | Boolean | Yes | N/A | Pulse | N/A
VoltaGrid Single Line Diagram | SYNCON | SC1 | SC_SC1_StartFailed_STAT | Yes | SC1 failed to start | Failure Message | Discrete Input | 0x02 | 11339 | 11339 | 1 | Boolean | No | N/A | N/A | N/A
VoltaGrid Single Line Diagram | SYNCON | SC1 | SC_SC1_StopFailed_STAT | Yes | SC1 failed to stop | Failure Message | Discrete Input | 0x02 | 11340 | 11340 | 1 | Boolean | No | N/A | N/A | N/A
VoltaGrid Single Line Diagram | SYNCON | SC1 | SC_SC1_CommFail_STAT | Yes | SC1 IED communication failure | Failure Message | Discrete Input | 0x02 | 11341 | 11341 | 1 | Boolean | No | N/A | N/A | N/A
VoltaGrid Single Line Diagram | SYNCON | SC2 | SC_SC2_StartFailed_STAT | Yes | SC2 failed to start | Failure Message | Discrete Input | 0x02 | 11342 | 11342 | 1 | Boolean | No | N/A | N/A | N/A
VoltaGrid Single Line Diagram | SYNCON | SC2 | SC_SC2_StopFailed_STAT | Yes | SC2 failed to stop | Failure Message | Discrete Input | 0x02 | 11343 | 11343 | 1 | Boolean | No | N/A | N/A | N/A
VoltaGrid Single Line Diagram | SYNCON | SC2 | SC_SC2_CommFail_STAT | Yes | SC2 IED communication failure | Failure Message | Discrete Input | 0x02 | 11344 | 11344 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | N/A | No | SPARE | Command | Coil | 0x05 | 377 | 377 | 1 | Boolean | Yes | N/A | N/A | N/A
N/A | N/A | N/A | SPARE | No | SPARE | Command | Coil | 0x05 | 538 | 538 | 1 | Boolean | Yes | N/A | N/A | N/A
N/A | N/A | N/A | N/A | Yes | SPARE |  | Discrete Input | 0x02 | 11047 | 11047 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | N/A | No | SPARE | Operation Message | Discrete Input | 0x02 | 11048 | 11048 | 1 | Boolean | No | N/A | N/A | N/A
Generation Management Control Screens | N\A | N\A | PMAX_PMAXEnabled_STAT | No | SPARE |  | Discrete Input | 0x02 | 11052 | 11052 | 1 | Boolean | No | N/A | Latch | 0=disabled, 1=enabled
Generation Management Control Screens | SYNCON | SC-1 | SC_SC1_Start_CMD | Yes | Start command for SynCon 1 | Command | Coil | 0x05 | 380 | 380 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | SYNCON | SC-2 | SC_SC2_Start_CMD | Yes | Start command for SynCon 2 | Command | Coil | 0x05 | 382 | 382 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | SYNCON | SC-1 | SC_SC1_Stop_CMD | Yes | Stop command for SynCon 1 | Command | Coil | 0x05 | 381 | 381 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens | SYNCON | SC-2 | SC_SC2_Stop_CMD | Yes | Stop command for SynCon 2 | Command | Coil | 0x05 | 383 | 383 | 1 | Boolean | Yes | N/A | Pulse | N/A
Generation Management Control Screens |  | SC-1 | SC_SC1_InOperation_STAT | Yes | Synchronous condenser 1 in operation | Operation Message | Discrete Input | 0x02 | 11054 | 11054 | 1 | Boolean | No | N/A | Latch
Generation Management Control Screens |  | SC-1 | SC_SC1_ReadyToStart_STAT | Yes | Synchronous condenser 1 ready to start | Operation Message | Discrete Input | 0x02 | 11053 | 11053 | 1 | Boolean | No | N/A | Latch
Generation Management Control Screens | SYNCON | SC-1 | SC_SC1_Stopped_STAT | Yes | Synchronous condenser 1 stopped | Operation Message | Discrete Input | 0x02 | 11055 | 11055 | 1 | Boolean | No | N/A | Latch
Generation Management Control Screens |  | SC-2 | SC_SC2_InOperation_STAT | Yes | Synchronous condenser 2 in operation | Operation Message | Discrete Input | 0x02 | 11057 | 11057 | 1 | Boolean | No | N/A | Latch
Generation Management Control Screens |  | SC-2 | SC_SC2_ReadyToStart_STAT | Yes | Synchronous condenser 2 ready to start | Operation Message | Discrete Input | 0x02 | 11056 | 11056 | 1 | Boolean | No | N/A | Latch
Generation Management Control Screens | SYNCON | SC-2 | SC_SC2_Stopped_STAT | Yes | Synchronous condenser 2 stopped | Operation Message | Discrete Input | 0x02 | 11058 | 11058 | 1 | Boolean | No | N/A | Latch
Generation Management Control Screens | N/A | N/A | GCS_RemoteBlock_CMD | Yes |  | Command | Coil | 0x05 | 376 | 376 | 1 | Boolean | Yes | N/A | Pulse | N/A | This should exist for all gens
VoltaGrid Single Line Diagram | N\A | N\A | EDG_BKR_Close_CMD | No |  | Command | Coil | 0x05 | 539 | 539 | 1 | Boolean | Yes | N/A | Pulse | N/A | Convert to Spare
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10006 | 10006 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10017 | 10017 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10027 | 10027 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-1 | G2 | VCS_G2_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10038 | 10038 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10048 | 10048 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-1 | G3 | VCS_G3_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10059 | 10059 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10069 | 10069 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-1 | G4 | VCS_G4_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10080 | 10080 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10090 | 10090 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-2 | G5 | VCS_G5_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10101 | 10101 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10111 | 10111 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-2 | G6 | VCS_G6_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10122 | 10122 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10132 | 10132 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-2 | G7 | VCS_G7_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10143 | 10143 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10153 | 10153 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-2 | G8 | VCS_G8_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10164 | 10164 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10174 | 10174 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-3 | G9 | VCS_G9_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10185 | 10185 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10195 | 10195 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10206 | 10206 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10216 | 10216 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10227 | 10227 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10237 | 10237 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10248 | 10248 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10258 | 10258 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10269 | 10269 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10279 | 10279 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10290 | 10290 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10300 | 10300 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10311 | 10311 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10321 | 10321 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10332 | 10332 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10342 | 10342 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10353 | 10353 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10363 | 10363 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10374 | 10374 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10384 | 10384 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10395 | 10395 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10405 | 10405 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-5 | G20 | VCS_G20_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10416 | 10416 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10426 | 10426 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-6 | G21 | VCS_G21_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10437 | 10437 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10447 | 10447 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-6 | G22 | VCS_G22_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10458 | 10458 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10468 | 10468 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-6 | G23 | VCS_G23_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10479 | 10479 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10489 | 10489 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-6 | G24 | VCS_G24_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10500 | 10500 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10510 | 10510 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-7 | G25 | VCS_G25_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10521 | 10521 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10531 | 10531 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-7 | G26 | VCS_G26_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10542 | 10542 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10552 | 10552 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-7 | G27 | VCS_G27_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10563 | 10563 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10573 | 10573 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-7 | G28 | VCS_G28_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10584 | 10584 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10594 | 10594 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-8 | G29 | VCS_G29_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10605 | 10605 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10615 | 10615 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-8 | G30 | VCS_G30_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10626 | 10626 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10636 | 10636 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-8 | G31 | VCS_G31_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10647 | 10647 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10657 | 10657 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-8 | G32 | VCS_G32_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10668 | 10668 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10678 | 10678 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-9 | G33 | VCS_G33_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10689 | 10689 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10699 | 10699 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-9 | G34 | VCS_G34_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10710 | 10710 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10720 | 10720 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-9 | G35 | VCS_G35_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10731 | 10731 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10741 | 10741 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-9 | G36 | VCS_G36_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10752 | 10752 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10762 | 10762 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-10 | G37 | VCS_G37_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10773 | 10773 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10783 | 10783 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-10 | G38 | VCS_G38_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10794 | 10794 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10804 | 10804 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-10 | G39 | VCS_G39_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10815 | 10815 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10825 | 10825 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-10 | G40 | VCS_G40_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10836 | 10836 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10846 | 10846 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-11 | G41 | VCS_G41_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10857 | 10857 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10867 | 10867 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-11 | G42 | VCS_G42_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10878 | 10878 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10888 | 10888 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-11 | G43 | VCS_G43_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10899 | 10899 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10909 | 10909 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-11 | G44 | VCS_G44_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10920 | 10920 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10930 | 10930 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-12 | G45 | VCS_G45_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10941 | 10941 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_GovernorAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10951 | 10951 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
Voltage Control System Screens | QPAC-12 | G46 | VCS_G46_ExciterAlarm_STAT | Yes |  | Failure Message | Discrete Input | 0x02 | 10962 | 10962 | 1 | Boolean | No | N/A | Latch | 0=normal, 1=alarm state
N/A | N/A | N/A | GMS_G1_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11151 | 11151 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G2_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11152 | 11152 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G3_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11153 | 11153 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G4_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11154 | 11154 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G5_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11155 | 11155 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G6_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11156 | 11156 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G7_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11157 | 11157 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G8_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11158 | 11158 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G9_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11159 | 11159 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G10_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11160 | 11160 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G11_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11161 | 11161 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G12_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11162 | 11162 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G13_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11163 | 11163 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G14_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11164 | 11164 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G15_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11165 | 11165 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G16_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11166 | 11166 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G17_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11167 | 11167 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G18_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11168 | 11168 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G19_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11169 | 11169 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G20_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11170 | 11170 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G21_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11171 | 11171 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G22_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11172 | 11172 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G23_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11173 | 11173 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G24_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11174 | 11174 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G25_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11175 | 11175 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G26_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11176 | 11176 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G27_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11177 | 11177 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G28_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11178 | 11178 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G29_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11179 | 11179 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G30_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11180 | 11180 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G31_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11181 | 11181 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G32_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11182 | 11182 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G33_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11183 | 11183 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G34_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11184 | 11184 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G35_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11185 | 11185 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G36_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11186 | 11186 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G37_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11187 | 11187 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G38_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11188 | 11188 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G39_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11189 | 11189 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G40_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11190 | 11190 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G41_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11191 | 11191 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G42_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11192 | 11192 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G43_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11193 | 11193 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G44_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11194 | 11194 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G45_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11195 | 11195 | 1 | Boolean | No | N/A | N/A | N/A
N/A | N/A | N/A | GMS_G46_AutoManualToggle_STAT | No |  |  | Discrete Input | 0x02 | 11196 | 11196 | 1 | Boolean | No | N/A | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Recovery_Step1_Status_VAL | Yes |  |  | Input Register | 0x04 | 31611 | 31611 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Recovery_Step2_Status_VAL | Yes |  |  | Input Register | 0x04 | 31612 | 31612 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Recovery_Step3_Status_VAL | Yes |  |  | Input Register | 0x04 | 31613 | 31613 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Recovery_Step4_Status_VAL | Yes |  |  | Input Register | 0x04 | 31614 | 31614 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step1_Status_VAL | Yes |  |  | Input Register | 0x04 | 31615 | 31615 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step2_Status_VAL | Yes |  |  | Input Register | 0x04 | 31616 | 31616 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step3_Status_VAL | Yes |  |  | Input Register | 0x04 | 31617 | 31617 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step4_Status_VAL | Yes |  |  | Input Register | 0x04 | 31618 | 31618 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step5_Status_VAL | Yes |  |  | Input Register | 0x04 | 31619 | 31619 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step6_Status_VAL | Yes |  |  | Input Register | 0x04 | 31620 | 31620 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step7_Status_VAL | Yes |  |  | Input Register | 0x04 | 31621 | 31621 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step8_Status_VAL | Yes |  |  | Input Register | 0x04 | 31622 | 31622 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step9_Status_VAL | Yes |  |  | Input Register | 0x04 | 31623 | 31623 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step10_Status_VAL | Yes |  |  | Input Register | 0x04 | 31624 | 31624 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step11_Status_VAL | Yes |  |  | Input Register | 0x04 | 31625 | 31625 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step12_Status_VAL | Yes |  |  | Input Register | 0x04 | 31626 | 31626 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step13_Status_VAL | Yes |  |  | Input Register | 0x04 | 31627 | 31627 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_Sequence_Step14_Status_VAL | Yes |  |  | Input Register | 0x04 | 31628 | 31628 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_NumberOfBlackstartGen_VAL | Yes |  |  | Input Register | 0x04 | 31629 | 31629 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_OpMode_VAL | Yes |  |  | Input Register | 0x04 | 31630 | 31630 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_ControlSwitchPos_VAL | Yes |  |  | Input Register | 0x04 | 31631 | 31631 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_OpState_VAL | Yes |  |  | Input Register | 0x04 | 31633 | 31633 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_AuxSwitchStatus_VAL | Yes |  |  | Input Register | 0x04 | 31634 | 31634 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | BS_StarterMode_VAL | Yes |  |  | Input Register | 0x04 | 31635 | 31635 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | N/A | N/A | GMS_IslandLowerCapacity_VAL | Yes |  |  | Input Register | 0x04 | 31636 | 31637 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Generation Management Control Screens | N/A | N/A | GMS_IslandRaiseCapacity_VAL | Yes |  |  | Input Register | 0x04 | 31638 | 31639 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Generation Management Control Screens | N/A | N/A | GMS_TotalGeneration_VAL | Yes |  |  | Input Register | 0x04 | 31640 | 31641 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Generation Management Control Screens | N/A | N/A | GMS_TotalCapacity_VAL | Yes |  |  | Input Register | 0x04 | 31642 | 31643 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Generation Management Control Screens | N/A | N/A | GMS_IslandLoading_VAL | Yes |  |  | Input Register | 0x04 | 31644 | 31645 | 2 | Float | No | 32 bit float MSR | % | 1 Unit = 1 %
Generation Management Control Screens | N/A | N/A | GMS_MinimumGensOnline_VAL | Yes |  |  | Input Register | 0x04 | 31646 | 31646 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | N/A | N/A | PMAX_AuxBusVoltage_VAL | Yes |  |  | Input Register | 0x04 | 31647 | 31648 | 2 | Float | No | 32 bit float MSR | kV | 1 Unit = 1 kV
Blackstart Sequence | N/A | N/A | PMAX_MainBusVoltage_VAL | Yes |  |  | Input Register | 0x04 | 31649 | 31650 | 2 | Float | No | 32 bit float MSR | kV | 1 Unit = 1 kV
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31653 | 31654 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31655 | 31656 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31657 | 31658 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31659 | 31660 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31661 | 31662 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31663 | 31664 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31665 | 31666 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31667 | 31668 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31669 | 31670 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31671 | 31672 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31673 | 31674 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31675 | 31676 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31677 | 31678 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31679 | 31680 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31681 | 31682 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31683 | 31684 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31685 | 31686 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31687 | 31688 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31689 | 31690 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31691 | 31692 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31693 | 31694 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31695 | 31696 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31697 | 31698 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31699 | 31700 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31701 | 31702 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31703 | 31704 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31705 | 31706 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31707 | 31708 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31709 | 31710 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31711 | 31712 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31713 | 31714 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31715 | 31716 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31717 | 31718 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31719 | 31720 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31721 | 31722 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31723 | 31724 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31725 | 31726 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31727 | 31728 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31729 | 31730 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31731 | 31732 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31733 | 31734 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31735 | 31736 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31737 | 31738 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31739 | 31740 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31741 | 31742 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31743 | 31744 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31745 | 31746 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31747 | 31748 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31749 | 31750 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31751 | 31752 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31753 | 31754 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31755 | 31756 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31757 | 31758 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31759 | 31760 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31761 | 31762 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31763 | 31764 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31765 | 31766 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31767 | 31768 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31769 | 31770 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31771 | 31772 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31773 | 31774 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31775 | 31776 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31777 | 31778 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31779 | 31780 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31781 | 31782 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31783 | 31784 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31785 | 31786 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31787 | 31788 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31789 | 31790 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31791 | 31792 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31793 | 31794 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31795 | 31796 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31797 | 31798 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31799 | 31800 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31801 | 31802 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31803 | 31804 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31805 | 31806 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31807 | 31808 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31809 | 31810 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31811 | 31812 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31813 | 31814 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31815 | 31816 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31817 | 31818 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31819 | 31820 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31821 | 31822 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31823 | 31824 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31825 | 31826 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31827 | 31828 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31829 | 31830 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31831 | 31832 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31833 | 31834 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31835 | 31836 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31837 | 31838 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31839 | 31840 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31841 | 31842 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31843 | 31844 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31845 | 31846 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31847 | 31848 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31849 | 31850 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31851 | 31852 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31853 | 31854 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31855 | 31856 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31857 | 31858 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31859 | 31860 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31861 | 31862 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31863 | 31864 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31865 | 31866 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31867 | 31868 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31869 | 31870 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31871 | 31872 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31873 | 31874 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31875 | 31876 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31877 | 31878 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31879 | 31880 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31881 | 31882 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31883 | 31884 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31885 | 31886 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31887 | 31888 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31889 | 31890 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31891 | 31892 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31893 | 31894 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31895 | 31896 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31897 | 31898 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31899 | 31900 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31901 | 31902 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31903 | 31904 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31905 | 31906 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31907 | 31908 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31909 | 31910 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31911 | 31912 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31913 | 31914 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31915 | 31916 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31917 | 31918 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31919 | 31920 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31921 | 31922 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31923 | 31924 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31925 | 31926 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31927 | 31928 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31929 | 31930 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31931 | 31932 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31933 | 31934 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31935 | 31936 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31937 | 31938 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31939 | 31940 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31941 | 31942 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31943 | 31944 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31945 | 31946 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31947 | 31948 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31949 | 31950 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31951 | 31952 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31953 | 31954 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31955 | 31956 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31957 | 31958 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31959 | 31960 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31961 | 31962 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31963 | 31964 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31965 | 31966 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31967 | 31968 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31969 | 31970 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31971 | 31972 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31973 | 31974 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31975 | 31976 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31977 | 31978 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31979 | 31980 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31981 | 31982 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31983 | 31984 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 31985 | 31986 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31987 | 31988 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31989 | 31990 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 31991 | 31992 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 31993 | 31994 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 31995 | 31996 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 31997 | 31998 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 31999 | 32000 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32001 | 32002 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32003 | 32004 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32005 | 32006 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32007 | 32008 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32009 | 32010 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32011 | 32012 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32013 | 32014 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32015 | 32016 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32017 | 32018 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32019 | 32020 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32021 | 32022 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32023 | 32024 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32025 | 32026 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32027 | 32028 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32029 | 32030 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32031 | 32032 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32033 | 32034 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32035 | 32036 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32037 | 32038 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32039 | 32040 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32041 | 32042 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32043 | 32044 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32045 | 32046 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32047 | 32048 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32049 | 32050 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32051 | 32052 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32053 | 32054 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32055 | 32056 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32057 | 32058 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32059 | 32060 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32061 | 32062 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32063 | 32064 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32065 | 32066 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32067 | 32068 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32069 | 32070 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32071 | 32072 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32073 | 32074 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32075 | 32076 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32077 | 32078 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32079 | 32080 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32081 | 32082 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32083 | 32084 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32085 | 32086 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32087 | 32088 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32089 | 32090 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32091 | 32092 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32093 | 32094 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32095 | 32096 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32097 | 32098 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32099 | 32100 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32101 | 32102 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32103 | 32104 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32105 | 32106 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32107 | 32108 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32109 | 32110 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32111 | 32112 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32113 | 32114 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32115 | 32116 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32117 | 32118 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32119 | 32120 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32121 | 32122 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32123 | 32124 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32125 | 32126 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32127 | 32128 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32129 | 32130 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32131 | 32132 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32133 | 32134 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32135 | 32136 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32137 | 32138 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32139 | 32140 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32141 | 32142 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32143 | 32144 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32145 | 32146 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32147 | 32148 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32149 | 32150 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32151 | 32152 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32153 | 32154 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32155 | 32156 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32157 | 32158 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32159 | 32160 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32161 | 32162 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32163 | 32164 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32165 | 32166 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32167 | 32168 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32169 | 32170 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32171 | 32172 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32173 | 32174 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32175 | 32176 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32177 | 32178 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32179 | 32180 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32181 | 32182 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32183 | 32184 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32185 | 32186 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32187 | 32188 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32189 | 32190 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32191 | 32192 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32193 | 32194 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32195 | 32196 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32197 | 32198 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32199 | 32200 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32201 | 32202 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32203 | 32204 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32205 | 32206 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32207 | 32208 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32209 | 32210 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32211 | 32212 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32213 | 32214 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32215 | 32216 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32217 | 32218 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32219 | 32220 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32221 | 32222 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32223 | 32224 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32225 | 32226 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32227 | 32228 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32229 | 32230 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32231 | 32232 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32233 | 32234 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32235 | 32236 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32237 | 32238 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32239 | 32240 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32241 | 32242 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32243 | 32244 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32245 | 32246 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32247 | 32248 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32249 | 32250 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32251 | 32252 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32253 | 32254 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32255 | 32256 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32257 | 32258 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32259 | 32260 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32261 | 32262 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32263 | 32264 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32265 | 32266 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32267 | 32268 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32269 | 32270 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32271 | 32272 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32273 | 32274 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32275 | 32276 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32277 | 32278 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32279 | 32280 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32281 | 32282 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32283 | 32284 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32285 | 32286 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32287 | 32288 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32289 | 32290 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32291 | 32292 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32293 | 32294 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32295 | 32296 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32297 | 32298 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32299 | 32300 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32301 | 32302 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32303 | 32304 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32305 | 32306 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32307 | 32308 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32309 | 32310 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32311 | 32312 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32313 | 32314 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32315 | 32316 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32317 | 32318 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32319 | 32320 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32321 | 32322 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32323 | 32324 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32325 | 32326 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32327 | 32328 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32329 | 32330 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32331 | 32332 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32333 | 32334 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32335 | 32336 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32337 | 32338 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32339 | 32340 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32341 | 32342 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32343 | 32344 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32345 | 32346 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32347 | 32348 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32349 | 32350 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32351 | 32352 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32353 | 32354 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32355 | 32356 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32357 | 32358 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32359 | 32360 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32361 | 32362 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32363 | 32364 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32365 | 32366 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32367 | 32368 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32369 | 32370 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32371 | 32372 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32373 | 32374 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32375 | 32376 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32377 | 32378 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32379 | 32380 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32381 | 32382 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32383 | 32384 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32385 | 32386 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32387 | 32388 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32389 | 32390 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32391 | 32392 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32393 | 32394 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32395 | 32396 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32397 | 32398 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32399 | 32400 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32401 | 32402 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32403 | 32404 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32405 | 32406 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32407 | 32408 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32409 | 32410 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32411 | 32412 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32413 | 32414 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32415 | 32416 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32417 | 32418 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32419 | 32420 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32421 | 32422 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32423 | 32424 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32425 | 32426 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32427 | 32428 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32429 | 32430 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32431 | 32432 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32433 | 32434 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32435 | 32436 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32437 | 32438 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32439 | 32440 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32441 | 32442 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32443 | 32444 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32445 | 32446 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32447 | 32448 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32449 | 32450 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32451 | 32452 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32453 | 32454 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32455 | 32456 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32457 | 32458 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32459 | 32460 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32461 | 32462 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32463 | 32464 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32465 | 32466 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32467 | 32468 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32469 | 32470 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32471 | 32472 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32473 | 32474 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32475 | 32476 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32477 | 32478 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32479 | 32480 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32481 | 32482 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32483 | 32484 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32485 | 32486 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32487 | 32488 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32489 | 32490 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32491 | 32492 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32493 | 32494 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32495 | 32496 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32497 | 32498 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32499 | 32500 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32501 | 32502 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32503 | 32504 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32505 | 32506 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32507 | 32508 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32509 | 32510 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32511 | 32512 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32513 | 32514 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32515 | 32516 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32517 | 32518 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32519 | 32520 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32521 | 32522 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32523 | 32524 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32525 | 32526 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32527 | 32528 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32529 | 32530 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32531 | 32532 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32533 | 32534 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32535 | 32536 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32537 | 32538 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32539 | 32540 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32541 | 32542 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32543 | 32544 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32545 | 32546 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32547 | 32548 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32549 | 32550 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32551 | 32552 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32553 | 32554 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32555 | 32556 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32557 | 32558 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32559 | 32560 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32561 | 32562 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32563 | 32564 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32565 | 32566 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32567 | 32568 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32569 | 32570 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32571 | 32572 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32573 | 32574 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32575 | 32576 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32577 | 32578 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32579 | 32580 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32581 | 32582 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32583 | 32584 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32585 | 32586 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32587 | 32588 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32589 | 32590 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32591 | 32592 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32593 | 32594 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32595 | 32596 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32597 | 32598 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32599 | 32600 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32601 | 32602 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32603 | 32604 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32605 | 32606 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32607 | 32608 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32609 | 32610 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32611 | 32612 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32613 | 32614 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32615 | 32616 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32617 | 32618 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32619 | 32620 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32621 | 32622 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32623 | 32624 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32625 | 32626 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32627 | 32628 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32629 | 32630 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32631 | 32632 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32633 | 32634 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32635 | 32636 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32637 | 32638 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32639 | 32640 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32641 | 32642 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32643 | 32644 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32645 | 32646 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32647 | 32648 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32649 | 32650 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32651 | 32652 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32653 | 32654 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32655 | 32656 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32657 | 32658 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32659 | 32660 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32661 | 32662 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32663 | 32664 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32665 | 32666 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32667 | 32668 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32669 | 32670 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32671 | 32672 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32673 | 32674 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32675 | 32676 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32677 | 32678 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32679 | 32680 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32681 | 32682 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32683 | 32684 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32685 | 32686 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32687 | 32688 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32689 | 32690 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32691 | 32692 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32693 | 32694 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32695 | 32696 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32697 | 32698 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32699 | 32700 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32701 | 32702 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32703 | 32704 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32705 | 32706 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32707 | 32708 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32709 | 32710 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32711 | 32712 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32713 | 32714 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32715 | 32716 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32717 | 32718 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32719 | 32720 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32721 | 32722 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32723 | 32724 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32725 | 32726 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32727 | 32728 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32729 | 32730 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32731 | 32732 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32733 | 32734 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32735 | 32736 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32737 | 32738 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32739 | 32740 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32741 | 32742 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32743 | 32744 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32745 | 32746 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32747 | 32748 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32749 | 32750 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32751 | 32752 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32753 | 32754 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32755 | 32756 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32757 | 32758 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32759 | 32760 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32761 | 32762 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32763 | 32764 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32765 | 32766 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32767 | 32768 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32769 | 32770 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32771 | 32772 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32773 | 32774 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32775 | 32776 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32777 | 32778 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32779 | 32780 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32781 | 32782 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32783 | 32784 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32785 | 32786 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32787 | 32788 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32789 | 32790 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32791 | 32792 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32793 | 32794 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32795 | 32796 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32797 | 32798 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32799 | 32800 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32801 | 32802 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32803 | 32804 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32805 | 32806 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32807 | 32808 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32809 | 32810 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32811 | 32812 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32813 | 32814 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32815 | 32816 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32817 | 32818 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32819 | 32820 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32821 | 32822 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32823 | 32824 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32825 | 32826 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32827 | 32828 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32829 | 32830 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32831 | 32832 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32833 | 32834 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32835 | 32836 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32837 | 32838 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32839 | 32840 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32841 | 32842 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32843 | 32844 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32845 | 32846 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32847 | 32848 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32849 | 32850 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32851 | 32852 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32853 | 32854 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32855 | 32856 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32857 | 32858 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32859 | 32860 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32861 | 32862 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32863 | 32864 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32865 | 32866 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32867 | 32868 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32869 | 32870 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32871 | 32872 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32873 | 32874 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32875 | 32876 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32877 | 32878 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32879 | 32880 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32881 | 32882 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32883 | 32884 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32885 | 32886 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32887 | 32888 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32889 | 32890 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32891 | 32892 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32893 | 32894 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32895 | 32896 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32897 | 32898 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32899 | 32900 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32901 | 32902 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32903 | 32904 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32905 | 32906 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32907 | 32908 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32909 | 32910 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32911 | 32912 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32913 | 32914 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32915 | 32916 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32917 | 32918 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32919 | 32920 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_DDB_Band_1_VAL | Yes |  |  | Input Register | 0x04 | 32921 | 32922 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_DDB_Wait_1_VAL | Yes |  |  | Input Register | 0x04 | 32923 | 32924 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_DDB_Band_2_VAL | Yes |  |  | Input Register | 0x04 | 32925 | 32926 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_DDB_Wait_2_VAL | Yes |  |  | Input Register | 0x04 | 32927 | 32928 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_Ramprate_VAL | Yes |  |  | Input Register | 0x04 | 32929 | 32930 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32931 | 32932 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32933 | 32934 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_V_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32935 | 32936 | 2 | Float | No | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_F_Deadband_VAL | Yes |  |  | Input Register | 0x04 | 32937 | 32938 | 2 | Float | No | 32 bit float MSR
Blackstart Sequence | N/A | N/A | PMAX_MainBusFrequency_VAL | Yes |  |  | Input Register | 0x04 | 32960 | 32961 | 2 | Float | No | 32 bit float MSR | Hz | 1 Unit = 1 Hz
Generation Management Control Screens | SYNCON | SC-1 | SC_S1_ActivePower_VAL | Yes |  |  | Input Register | 0x04 | 32962 | 32963 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Generation Management Control Screens | SYNCON | SC-1 | SC_S1_ReactivePower_VAL | Yes |  |  | Input Register | 0x04 | 32964 | 32965 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Generation Management Control Screens | SYNCON | SC-2 | SC_S2_ActivePower_VAL | Yes |  |  | Input Register | 0x04 | 32966 | 32967 | 2 | Float | No | 32 bit float MSR | MW | 1 Unit = 1 MW
Generation Management Control Screens | SYNCON | SC-2 | SC_S2_ReactivePower_VAL | Yes |  |  | Input Register | 0x04 | 32968 | 32969 | 2 | Float | No | 32 bit float MSR | MVAR | 1 Unit = 1 MVAR
Generation Management Control Screens | N/A | N/A | GMS_NextGenToStart_VAL | Yes |  |  | Input Register | 0x04 | 2971 | 2971 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | N/A | N/A | GMS_NextGenToStart2_VAL | Yes |  |  | Input Register | 0x04 | 2972 | 2972 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | N/A | N/A | GMS_NextGenToStop_VAL | Yes |  |  | Input Register | 0x04 | 2973 | 2973 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | N/A | N/A | GMS_ActualIsRaiseCap_VAL | Yes |  |  | Input Register | 0x04 | 2974 | 2975 | 2 | Float | No | 32 bit float MSR | N/A | N/A
Generation Management Control Screens | N/A | N/A | GMS_ActualIsLowerCap_VAL | Yes |  |  | Input Register | 0x04 | 2976 | 2977 | 2 | Float | No | 32 bit float MSR | N/A | N/A
VoltaGrid Single Line Diagram | SYNCON | SC-1 | GCS_SC1_OpStatus_VAL | Yes |  |  | Input Register | 0x04 | 2980 | 2980 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
VoltaGrid Single Line Diagram | SYNCON | SC-2 | GCS_SC2_OpStatus_VAL | Yes |  |  | Input Register | 0x04 | 2981 | 2981 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus A) | N/A | PMAX_EHouseBusAVoltage_VAL | Yes |  |  | Input Register | 0x04 | 2982 | 2983 | 2 | Float | No | 32 bit float MSR | N/A | N/A
VoltaGrid Single Line Diagram | Auxiliary E-House (Bus B) | N/A | PMAX_EHouseBusBVoltage_VAL | Yes |  |  | Input Register | 0x04 | 2984 | 2985 | 2 | Float | No | 32 bit float MSR | N/A | N/A
N/A | N/A | N/A | SPARE | No |  |  | Input Register | 0x04 | 2988 | 2989 | 2 | Float | No | 32 bit float MSR | N/A | N/A
VoltaGrid Single Line Diagram | N/A | N/A | PMAX_TotalGensOnline_VAL | Yes |  |  | Input Register | 0x04 | 2990 | 2990 | 1 | Int | No | 16 bit signed MSB | N/A | N/A
Blackstart Sequence | Auxiliary E-House | EDG | BS_EDG_ActivePower_VAL | Yes |  |  | Input Register | 0x04 | 2991 | 2992 | 2 | Float | No | 32 bit float MSR | N/A | N/A
Blackstart Sequence | Auxiliary E-House | EDG | BS_EDG_ReactivePower_VAL | Yes |  |  | Input Register | 0x04 | 2993 | 2994 | 2 | Float | No | 32 bit float MSR | N/A | N/A
Generation Management Control Screens | N/A | N/A | SystemInertia_VAL | Yes |  |  | Input Register | 0x04 | 3041 | 3042 | 2 | Float | No | 32 bit float MSR | N/A | N/A
Generation Management Control Screens | N/A | N/A | GMS_IslandLowerCapacity_SET | Yes |  |  | Holding Register | 0x10 | 40606 | 40607 | 2 | Float | Yes | 32 bit float MSR
Generation Management Control Screens | N/A | N/A | GMS_IslandRaiseCapacity_SET | Yes |  |  | Holding Register | 0x10 | 40608 | 40609 | 2 | Float | Yes | 32 bit float MSR
Generation Management Control Screens | N/A | N/A | GMS_MinimumGensOnline_SET | Yes |  |  | Holding Register | 0x06 | 40610 | 40610 | 1 | Int | Yes | 16 bit signed MSB | N/A | N/A
Generation Management Control Screens | N/A | N/A | GMS_IslandReserveMargin_SET | Yes |  |  | Holding Register | 0x10 | 40611 | 40612 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40620 | 40621 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40622 | 40623 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40624 | 40625 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40626 | 40627 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40628 | 40629 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40630 | 40631 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40632 | 40633 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40634 | 40635 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40636 | 40637 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40638 | 40639 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40640 | 40641 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40642 | 40643 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40644 | 40645 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN1 | GT_G1_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40646 | 40647 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40648 | 40649 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40650 | 40651 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40652 | 40653 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40654 | 40655 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40656 | 40657 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40658 | 40659 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40660 | 40661 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40662 | 40663 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40664 | 40665 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40666 | 40667 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40668 | 40669 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40670 | 40671 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40672 | 40673 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN2 | GT_G2_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40674 | 40675 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40676 | 40677 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40678 | 40679 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40680 | 40681 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40682 | 40683 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40684 | 40685 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40686 | 40687 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40688 | 40689 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40690 | 40691 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40692 | 40693 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40694 | 40695 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40696 | 40697 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40698 | 40699 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40700 | 40701 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN3 | GT_G3_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40702 | 40703 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40704 | 40705 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40706 | 40707 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40708 | 40709 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40710 | 40711 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40712 | 40713 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40714 | 40715 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40716 | 40717 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40718 | 40719 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40720 | 40721 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40722 | 40723 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40724 | 40725 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40726 | 40727 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40728 | 40729 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-1 | GEN4 | GT_G4_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40730 | 40731 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40732 | 40733 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40734 | 40735 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40736 | 40737 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40738 | 40739 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40740 | 40741 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40742 | 40743 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40744 | 40745 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40746 | 40747 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40748 | 40749 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40750 | 40751 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40752 | 40753 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40754 | 40755 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40756 | 40757 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN5 | GT_G5_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40758 | 40759 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40760 | 40761 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40762 | 40763 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40764 | 40765 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40766 | 40767 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40768 | 40769 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40770 | 40771 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40772 | 40773 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40774 | 40775 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40776 | 40777 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40778 | 40779 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40780 | 40781 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40782 | 40783 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40784 | 40785 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN6 | GT_G6_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40786 | 40787 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40788 | 40789 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40790 | 40791 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40792 | 40793 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40794 | 40795 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40796 | 40797 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40798 | 40799 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40800 | 40801 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40802 | 40803 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40804 | 40805 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40806 | 40807 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40808 | 40809 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40810 | 40811 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40812 | 40813 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN7 | GT_G7_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40814 | 40815 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40816 | 40817 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40818 | 40819 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40820 | 40821 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40822 | 40823 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40824 | 40825 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40826 | 40827 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40828 | 40829 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40830 | 40831 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40832 | 40833 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40834 | 40835 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40836 | 40837 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40838 | 40839 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40840 | 40841 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-2 | GEN8 | GT_G8_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40842 | 40843 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40844 | 40845 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40846 | 40847 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40848 | 40849 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40850 | 40851 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40852 | 40853 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40854 | 40855 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40856 | 40857 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40858 | 40859 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40860 | 40861 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40862 | 40863 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40864 | 40865 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40866 | 40867 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40868 | 40869 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN9 | GT_G9_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40870 | 40871 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40872 | 40873 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40874 | 40875 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40876 | 40877 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40878 | 40879 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40880 | 40881 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40882 | 40883 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40884 | 40885 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40886 | 40887 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40888 | 40889 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40890 | 40891 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40892 | 40893 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40894 | 40895 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40896 | 40897 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN10 | GT_G10_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40898 | 40899 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40900 | 40901 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40902 | 40903 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40904 | 40905 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40906 | 40907 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40908 | 40909 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40910 | 40911 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40912 | 40913 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40914 | 40915 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40916 | 40917 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40918 | 40919 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40920 | 40921 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40922 | 40923 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40924 | 40925 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN11 | GT_G11_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40926 | 40927 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40928 | 40929 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40930 | 40931 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40932 | 40933 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40934 | 40935 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40936 | 40937 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40938 | 40939 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40940 | 40941 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40942 | 40943 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40944 | 40945 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40946 | 40947 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40948 | 40949 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40950 | 40951 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40952 | 40953 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-3 | GEN12 | GT_G12_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40954 | 40955 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40956 | 40957 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40958 | 40959 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40960 | 40961 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40962 | 40963 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40964 | 40965 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40966 | 40967 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40968 | 40969 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40970 | 40971 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40972 | 40973 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40974 | 40975 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40976 | 40977 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40978 | 40979 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40980 | 40981 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN13 | GT_G13_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40982 | 40983 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40984 | 40985 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40986 | 40987 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40988 | 40989 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40990 | 40991 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40992 | 40993 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40994 | 40995 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40996 | 40997 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 40998 | 40999 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41000 | 41001 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41002 | 41003 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41004 | 41005 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41006 | 41007 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41008 | 41009 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN14 | GT_G14_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41010 | 41011 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41012 | 41013 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41014 | 41015 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41016 | 41017 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41018 | 41019 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41020 | 41021 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41022 | 41023 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41024 | 41025 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41026 | 41027 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41028 | 41029 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41030 | 41031 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41032 | 41033 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41034 | 41035 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41036 | 41037 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN15 | GT_G15_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41038 | 41039 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41040 | 41041 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41042 | 41043 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41044 | 41045 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41046 | 41047 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41048 | 41049 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41050 | 41051 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41052 | 41053 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41054 | 41055 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41056 | 41057 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41058 | 41059 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41060 | 41061 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41062 | 41063 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41064 | 41065 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-4 | GEN16 | GT_G16_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41066 | 41067 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41068 | 41069 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41070 | 41071 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41072 | 41073 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41074 | 41075 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41076 | 41077 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41078 | 41079 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41080 | 41081 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41082 | 41083 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41084 | 41085 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41086 | 41087 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41088 | 41089 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41090 | 41091 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41092 | 41093 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN17 | GT_G17_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41094 | 41095 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41096 | 41097 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41098 | 41099 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41100 | 41101 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41102 | 41103 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41104 | 41105 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41106 | 41107 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41108 | 41109 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41110 | 41111 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41112 | 41113 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41114 | 41115 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41116 | 41117 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41118 | 41119 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41120 | 41121 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN18 | GT_G18_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41122 | 41123 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41124 | 41125 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41126 | 41127 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41128 | 41129 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41130 | 41131 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41132 | 41133 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41134 | 41135 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41136 | 41137 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41138 | 41139 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41140 | 41141 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41142 | 41143 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41144 | 41145 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41146 | 41147 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41148 | 41149 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN19 | GT_G19_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41150 | 41151 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41152 | 41153 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41154 | 41155 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41156 | 41157 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41158 | 41159 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41160 | 41161 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41162 | 41163 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41164 | 41165 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41166 | 41167 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41168 | 41169 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41170 | 41171 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41172 | 41173 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41174 | 41175 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41176 | 41177 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-5 | GEN20 | GT_G20_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41178 | 41179 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41180 | 41181 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41182 | 41183 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41184 | 41185 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41186 | 41187 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41188 | 41189 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41190 | 41191 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41192 | 41193 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41194 | 41195 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41196 | 41197 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41198 | 41199 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41200 | 41201 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41202 | 41203 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41204 | 41205 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN21 | GT_G21_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41206 | 41207 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41208 | 41209 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41210 | 41211 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41212 | 41213 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41214 | 41215 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41216 | 41217 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41218 | 41219 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41220 | 41221 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41222 | 41223 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41224 | 41225 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41226 | 41227 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41228 | 41229 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41230 | 41231 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41232 | 41233 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN22 | GT_G22_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41234 | 41235 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41236 | 41237 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41238 | 41239 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41240 | 41241 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41242 | 41243 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41244 | 41245 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41246 | 41247 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41248 | 41249 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41250 | 41251 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41252 | 41253 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41254 | 41255 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41256 | 41257 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41258 | 41259 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41260 | 41261 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN23 | GT_G23_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41262 | 41263 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41264 | 41265 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41266 | 41267 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41268 | 41269 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41270 | 41271 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41272 | 41273 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41274 | 41275 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41276 | 41277 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41278 | 41279 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41280 | 41281 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41282 | 41283 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41284 | 41285 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41286 | 41287 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41288 | 41289 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-6 | GEN24 | GT_G24_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41290 | 41291 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41292 | 41293 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41294 | 41295 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41296 | 41297 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41298 | 41299 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41300 | 41301 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41302 | 41303 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41304 | 41305 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41306 | 41307 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41308 | 41309 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41310 | 41311 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41312 | 41313 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41314 | 41315 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41316 | 41317 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN25 | GT_G25_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41318 | 41319 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41320 | 41321 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41322 | 41323 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41324 | 41325 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41326 | 41327 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41328 | 41329 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41330 | 41331 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41332 | 41333 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41334 | 41335 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41336 | 41337 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41338 | 41339 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41340 | 41341 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41342 | 41343 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41344 | 41345 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN26 | GT_G26_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41346 | 41347 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41348 | 41349 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41350 | 41351 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41352 | 41353 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41354 | 41355 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41356 | 41357 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41358 | 41359 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41360 | 41361 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41362 | 41363 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41364 | 41365 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41366 | 41367 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41368 | 41369 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41370 | 41371 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41372 | 41373 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN27 | GT_G27_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41374 | 41375 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41376 | 41377 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41378 | 41379 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41380 | 41381 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41382 | 41383 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41384 | 41385 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41386 | 41387 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41388 | 41389 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41390 | 41391 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41392 | 41393 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41394 | 41395 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41396 | 41397 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41398 | 41399 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41400 | 41401 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-7 | GEN28 | GT_G28_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41402 | 41403 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41404 | 41405 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41406 | 41407 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41408 | 41409 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41410 | 41411 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41412 | 41413 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41414 | 41415 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41416 | 41417 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41418 | 41419 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41420 | 41421 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41422 | 41423 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41424 | 41425 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41426 | 41427 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41428 | 41429 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN29 | GT_G29_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41430 | 41431 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41432 | 41433 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41434 | 41435 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41436 | 41437 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41438 | 41439 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41440 | 41441 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41442 | 41443 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41444 | 41445 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41446 | 41447 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41448 | 41449 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41450 | 41451 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41452 | 41453 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41454 | 41455 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41456 | 41457 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN30 | GT_G30_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41458 | 41459 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41460 | 41461 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41462 | 41463 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41464 | 41465 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41466 | 41467 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41468 | 41469 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41470 | 41471 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41472 | 41473 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41474 | 41475 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41476 | 41477 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41478 | 41479 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41480 | 41481 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41482 | 41483 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41484 | 41485 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN31 | GT_G31_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41486 | 41487 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41488 | 41489 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41490 | 41491 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41492 | 41493 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41494 | 41495 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41496 | 41497 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41498 | 41499 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41500 | 41501 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41502 | 41503 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41504 | 41505 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41506 | 41507 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41508 | 41509 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41510 | 41511 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41512 | 41513 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-8 | GEN32 | GT_G32_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41514 | 41515 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41516 | 41517 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41518 | 41519 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41520 | 41521 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41522 | 41523 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41524 | 41525 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41526 | 41527 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41528 | 41529 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41530 | 41531 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41532 | 41533 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41534 | 41535 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41536 | 41537 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41538 | 41539 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41540 | 41541 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN33 | GT_G33_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41542 | 41543 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41544 | 41545 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41546 | 41547 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41548 | 41549 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41550 | 41551 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41552 | 41553 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41554 | 41555 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41556 | 41557 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41558 | 41559 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41560 | 41561 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41562 | 41563 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41564 | 41565 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41566 | 41567 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41568 | 41569 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN34 | GT_G34_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41570 | 41571 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41572 | 41573 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41574 | 41575 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41576 | 41577 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41578 | 41579 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41580 | 41581 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41582 | 41583 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41584 | 41585 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41586 | 41587 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41588 | 41589 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41590 | 41591 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41592 | 41593 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41594 | 41595 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41596 | 41597 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN35 | GT_G35_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41598 | 41599 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41600 | 41601 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41602 | 41603 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41604 | 41605 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41606 | 41607 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41608 | 41609 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41610 | 41611 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41612 | 41613 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41614 | 41615 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41616 | 41617 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41618 | 41619 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41620 | 41621 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41622 | 41623 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41624 | 41625 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-9 | GEN36 | GT_G36_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41626 | 41627 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41628 | 41629 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41630 | 41631 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41632 | 41633 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41634 | 41635 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41636 | 41637 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41638 | 41639 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41640 | 41641 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41642 | 41643 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41644 | 41645 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41646 | 41647 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41648 | 41649 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41650 | 41651 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41652 | 41653 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN37 | GT_G37_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41654 | 41655 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41656 | 41657 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41658 | 41659 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41660 | 41661 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41662 | 41663 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41664 | 41665 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41666 | 41667 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41668 | 41669 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41670 | 41671 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41672 | 41673 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41674 | 41675 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41676 | 41677 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41678 | 41679 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41680 | 41681 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN38 | GT_G38_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41682 | 41683 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41684 | 41685 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41686 | 41687 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41688 | 41689 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41690 | 41691 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41692 | 41693 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41694 | 41695 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41696 | 41697 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41698 | 41699 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41700 | 41701 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41702 | 41703 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41704 | 41705 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41706 | 41707 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41708 | 41709 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN39 | GT_G39_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41710 | 41711 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41712 | 41713 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41714 | 41715 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41716 | 41717 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41718 | 41719 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41720 | 41721 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41722 | 41723 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41724 | 41725 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41726 | 41727 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41728 | 41729 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41730 | 41731 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41732 | 41733 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41734 | 41735 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41736 | 41737 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-10 | GEN40 | GT_G40_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41738 | 41739 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41740 | 41741 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41742 | 41743 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41744 | 41745 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41746 | 41747 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41748 | 41749 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41750 | 41751 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41752 | 41753 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41754 | 41755 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41756 | 41757 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41758 | 41759 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41760 | 41761 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41762 | 41763 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41764 | 41765 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN41 | GT_G41_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41766 | 41767 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41768 | 41769 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41770 | 41771 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41772 | 41773 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41774 | 41775 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41776 | 41777 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41778 | 41779 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41780 | 41781 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41782 | 41783 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41784 | 41785 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41786 | 41787 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41788 | 41789 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41790 | 41791 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41792 | 41793 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN42 | GT_G42_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41794 | 41795 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41796 | 41797 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41798 | 41799 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41800 | 41801 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41802 | 41803 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41804 | 41805 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41806 | 41807 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41808 | 41809 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41810 | 41811 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41812 | 41813 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41814 | 41815 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41816 | 41817 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41818 | 41819 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41820 | 41821 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN43 | GT_G43_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41822 | 41823 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41824 | 41825 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41826 | 41827 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41828 | 41829 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41830 | 41831 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41832 | 41833 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41834 | 41835 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41836 | 41837 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41838 | 41839 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41840 | 41841 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41842 | 41843 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41844 | 41845 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41846 | 41847 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41848 | 41849 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-11 | GEN44 | GT_G44_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41850 | 41851 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41852 | 41853 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41854 | 41855 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41856 | 41857 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41858 | 41859 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41860 | 41861 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41862 | 41863 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41864 | 41865 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41866 | 41867 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41868 | 41869 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41870 | 41871 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41872 | 41873 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41874 | 41875 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41876 | 41877 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN45 | GT_G45_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41878 | 41879 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41880 | 41881 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41882 | 41883 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41884 | 41885 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41886 | 41887 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41888 | 41889 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_DDB_Band_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41890 | 41891 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_DDB_Wait_1_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41892 | 41893 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_DDB_Band_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41894 | 41895 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_DDB_Wait_2_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41896 | 41897 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_Ramprate_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41898 | 41899 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_P_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41900 | 41901 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_Q_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41902 | 41903 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_V_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41904 | 41905 | 2 | Float | Yes | 32 bit float MSR
Generator Tuning Screen | QPAC-12 | GEN46 | GT_G46_F_Deadband_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 41906 | 41907 | 2 | Float | Yes | 32 bit float MSR
Voltage Control System Screens | SYNCON | N/A | SC_GenPFObj_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1907 | 1908 | 2 | Float | Yes | 32 bit float MSR | N/A
Generation Management Control Screens | QPAC-1 | GEN1 | GMS_G1_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1911 | 1911 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-1 | GEN2 | GMS_G2_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1912 | 1912 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-1 | GEN3 | GMS_G3_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1913 | 1913 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-1 | GEN4 | GMS_G4_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1914 | 1914 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-2 | GEN5 | GMS_G5_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1915 | 1915 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-2 | GEN6 | GMS_G6_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1916 | 1916 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-2 | GEN7 | GMS_G7_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1917 | 1917 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-2 | GEN8 | GMS_G8_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1918 | 1918 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-3 | GEN9 | GMS_G9_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1919 | 1919 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-3 | GEN10 | GMS_G10_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1920 | 1920 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-3 | GEN11 | GMS_G11_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1921 | 1921 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-3 | GEN12 | GMS_G12_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1922 | 1922 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-4 | GEN13 | GMS_G13_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1923 | 1923 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-4 | GEN14 | GMS_G14_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1924 | 1924 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-4 | GEN15 | GMS_G15_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1925 | 1925 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-4 | GEN16 | GMS_G16_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1926 | 1926 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-5 | GEN17 | GMS_G17_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1927 | 1927 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-5 | GEN18 | GMS_G18_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1928 | 1928 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-5 | GEN19 | GMS_G19_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1929 | 1929 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-5 | GEN20 | GMS_G20_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1930 | 1930 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-6 | GEN21 | GMS_G21_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1931 | 1931 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-6 | GEN22 | GMS_G22_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1932 | 1932 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-6 | GEN23 | GMS_G23_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1933 | 1933 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-6 | GEN24 | GMS_G24_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1934 | 1934 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-7 | GEN25 | GMS_G25_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1935 | 1935 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-7 | GEN26 | GMS_G26_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1936 | 1936 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-7 | GEN27 | GMS_G27_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1937 | 1937 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-7 | GEN28 | GMS_G28_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1938 | 1938 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-8 | GEN29 | GMS_G29_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1939 | 1939 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-8 | GEN30 | GMS_G30_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1940 | 1940 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-8 | GEN31 | GMS_G31_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1941 | 1941 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-8 | GEN32 | GMS_G32_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1942 | 1942 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-9 | GEN33 | GMS_G33_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1943 | 1943 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-9 | GEN34 | GMS_G34_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1944 | 1944 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-9 | GEN35 | GMS_G35_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1945 | 1945 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-9 | GEN36 | GMS_G36_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1946 | 1946 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-10 | GEN37 | GMS_G37_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1947 | 1947 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-10 | GEN38 | GMS_G38_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1948 | 1948 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-10 | GEN39 | GMS_G39_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1949 | 1949 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-10 | GEN40 | GMS_G40_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1950 | 1950 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-11 | GEN41 | GMS_G41_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1951 | 1951 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-11 | GEN42 | GMS_G42_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1952 | 1952 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-11 | GEN43 | GMS_G43_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1953 | 1953 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-11 | GEN44 | GMS_G44_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1954 | 1954 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-12 | GEN45 | GMS_G45_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1955 | 1955 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Generation Management Control Screens | QPAC-12 | GEN46 | GMS_G46_GensetOpMode_SET | Yes |  | Control Setpoint | Holding Register | 0x10 | 1956 | 1956 | 1 | Int | Yes | 16 bit signed MSB | N/A | 0=manual, 1=auto, 2=block
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_FollowingError_STAT | Yes | Alarm from Controller if genset is not following MVAR setpoint when controller is master
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN1 SEL-2411
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN2 SEL-2411
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN3 SEL-2411
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN4 SEL-2411
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN5 SEL-2411
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN6 SEL-2411
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN7 SEL-2411
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN8 SEL-2411
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN9 SEL-2411
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN10 SEL-2411
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN11 SEL-2411
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN12 SEL-2411
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN13 SEL-2411
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN14 SEL-2411
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN15 SEL-2411
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN16 SEL-2411
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN17 SEL-2411
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN18 SEL-2411
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN19 SEL-2411
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN20 SEL-2411
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN21 SEL-2411
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN22 SEL-2411
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN23 SEL-2411
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN24 SEL-2411
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN25 SEL-2411
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN26 SEL-2411
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN27 SEL-2411
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN28 SEL-2411
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN29 SEL-2411
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN30 SEL-2411
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN31 SEL-2411
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN32 SEL-2411
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN33 SEL-2411
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN34 SEL-2411
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN35 SEL-2411
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN36 SEL-2411
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN37 SEL-2411
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN38 SEL-2411
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN39 SEL-2411
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN40 SEL-2411
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN41 SEL-2411
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN42 SEL-2411
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN43 SEL-2411
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN44 SEL-2411
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN45 SEL-2411
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_2411BKROpFail_STAT | Yes | Breaker Op. Failure from GEN46 SEL-2411
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_AutoManual_CMD | Yes | Command to set genset in Auto/Manual control by PowerMAX Controller
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G1
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G2
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G3
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G4
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G5
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G6
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G7
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G8
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G9
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G10
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G11
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G12
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G13
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G14
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G15
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G16
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G17
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G18
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G19
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G20
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G21
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G22
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G23
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G24
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G25
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G26
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G27
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G28
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G29
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G30
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G31
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G32
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G33
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G34
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G35
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G36
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G37
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G38
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G39
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G40
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G41
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G42
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G43
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G44
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G45
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_BaseSetpoint_VAL | Yes | Current MVAR Manual setpoint in controller for G46
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G1
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G2
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G3
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G4
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G5
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G6
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G7
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G8
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G9
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G10
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G11
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G12
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G13
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G14
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G15
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G16
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G17
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G18
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G19
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G20
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G21
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G22
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G23
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G24
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G25
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G26
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G27
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G28
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G29
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G30
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G31
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G32
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G33
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G34
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G35
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G36
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G37
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G38
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G39
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G40
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G41
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G42
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G43
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G44
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G45
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_RequestedSetpoint_VAL | Yes | Current MVAR requested setpoint from controller for G46
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_CommFail_STAT | Yes | Unhealthy communications with gen IEDs
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN1
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN10
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN11
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN12
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN13
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN14
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN15
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN16
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN17
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN18
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN19
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN2
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN20
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN21
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN22
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN23
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN24
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN25
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN26
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN27
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN28
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN29
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN3
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN30
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN31
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN32
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN33
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN34
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN35
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN36
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN37
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN38
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN39
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN4
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN40
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN41
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN42
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN43
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN44
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN45
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN46
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN5
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN6
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN7
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN8
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_LowerRegLimit_VAL | Yes | Current MVAR lower regulation limit in controller for GEN9
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G1
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G2
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G3
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G4
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G5
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G6
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G7
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G8
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G9
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G10
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G11
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G12
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G13
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G14
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G15
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G16
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G17
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G18
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G19
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G20
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G21
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G22
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G23
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G24
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G25
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G26
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G27
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G28
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G29
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G30
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G31
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G32
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G33
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G34
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G35
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G36
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G37
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G38
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G39
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G40
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G41
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G42
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G43
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G44
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G45
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_BaseSetpoint_VAL | Yes | Current MW Manual setpoint in controller for G46
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G1
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G2
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G3
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G4
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G5
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G6
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G7
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G8
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G9
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G10
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G11
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G12
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G13
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G14
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G15
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G16
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G17
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G18
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G19
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G20
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G21
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G22
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G23
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G24
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G25
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G26
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G27
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G28
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G29
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G30
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G31
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G32
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G33
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G34
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G35
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G36
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G37
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G38
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G39
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G40
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G41
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G42
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G43
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G44
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G45
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_RequestedSetpoint_VAL | Yes | Current MW requested setpoint from controller for G46
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_Voltage_VAL | Yes | Voltage (kV) from field for G1
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_Voltage_VAL | Yes | Voltage (kV) from field for G2
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_Voltage_VAL | Yes | Voltage (kV) from field for G3
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_Voltage_VAL | Yes | Voltage (kV) from field for G4
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_Voltage_VAL | Yes | Voltage (kV) from field for G5
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_Voltage_VAL | Yes | Voltage (kV) from field for G6
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_Voltage_VAL | Yes | Voltage (kV) from field for G7
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_Voltage_VAL | Yes | Voltage (kV) from field for G8
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_Voltage_VAL | Yes | Voltage (kV) from field for G9
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_Voltage_VAL | Yes | Voltage (kV) from field for G10
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_Voltage_VAL | Yes | Voltage (kV) from field for G11
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_Voltage_VAL | Yes | Voltage (kV) from field for G12
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_Voltage_VAL | Yes | Voltage (kV) from field for G13
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_Voltage_VAL | Yes | Voltage (kV) from field for G14
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_Voltage_VAL | Yes | Voltage (kV) from field for G15
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_Voltage_VAL | Yes | Voltage (kV) from field for G16
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_Voltage_VAL | Yes | Voltage (kV) from field for G17
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_Voltage_VAL | Yes | Voltage (kV) from field for G18
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_Voltage_VAL | Yes | Voltage (kV) from field for G19
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_Voltage_VAL | Yes | Voltage (kV) from field for G20
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_Voltage_VAL | Yes | Voltage (kV) from field for G21
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_Voltage_VAL | Yes | Voltage (kV) from field for G22
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_Voltage_VAL | Yes | Voltage (kV) from field for G23
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_Voltage_VAL | Yes | Voltage (kV) from field for G24
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_Voltage_VAL | Yes | Voltage (kV) from field for G25
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_Voltage_VAL | Yes | Voltage (kV) from field for G26
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_Voltage_VAL | Yes | Voltage (kV) from field for G27
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_Voltage_VAL | Yes | Voltage (kV) from field for G28
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_Voltage_VAL | Yes | Voltage (kV) from field for G29
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_Voltage_VAL | Yes | Voltage (kV) from field for G30
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_Voltage_VAL | Yes | Voltage (kV) from field for G31
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_Voltage_VAL | Yes | Voltage (kV) from field for G32
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_Voltage_VAL | Yes | Voltage (kV) from field for G33
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_Voltage_VAL | Yes | Voltage (kV) from field for G34
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_Voltage_VAL | Yes | Voltage (kV) from field for G35
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_Voltage_VAL | Yes | Voltage (kV) from field for G36
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_Voltage_VAL | Yes | Voltage (kV) from field for G37
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_Voltage_VAL | Yes | Voltage (kV) from field for G38
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_Voltage_VAL | Yes | Voltage (kV) from field for G39
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_Voltage_VAL | Yes | Voltage (kV) from field for G40
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_Voltage_VAL | Yes | Voltage (kV) from field for G41
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_Voltage_VAL | Yes | Voltage (kV) from field for G42
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_Voltage_VAL | Yes | Voltage (kV) from field for G43
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_Voltage_VAL | Yes | Voltage (kV) from field for G44
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_Voltage_VAL | Yes | Voltage (kV) from field for G45
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_Voltage_VAL | Yes | Voltage (kV) from field for G46
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_EngineRuntime_VAL | Yes | Engine operating time in hours for G1
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_EngineRuntime_VAL | Yes | Engine operating time in hours for G2
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_EngineRuntime_VAL | Yes | Engine operating time in hours for G3
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_EngineRuntime_VAL | Yes | Engine operating time in hours for G4
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_EngineRuntime_VAL | Yes | Engine operating time in hours for G5
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_EngineRuntime_VAL | Yes | Engine operating time in hours for G6
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_EngineRuntime_VAL | Yes | Engine operating time in hours for G7
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_EngineRuntime_VAL | Yes | Engine operating time in hours for G8
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_EngineRuntime_VAL | Yes | Engine operating time in hours for G9
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_EngineRuntime_VAL | Yes | Engine operating time in hours for G10
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_EngineRuntime_VAL | Yes | Engine operating time in hours for G11
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_EngineRuntime_VAL | Yes | Engine operating time in hours for G12
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_EngineRuntime_VAL | Yes | Engine operating time in hours for G13
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_EngineRuntime_VAL | Yes | Engine operating time in hours for G14
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_EngineRuntime_VAL | Yes | Engine operating time in hours for G15
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_EngineRuntime_VAL | Yes | Engine operating time in hours for G16
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_EngineRuntime_VAL | Yes | Engine operating time in hours for G17
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_EngineRuntime_VAL | Yes | Engine operating time in hours for G18
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_EngineRuntime_VAL | Yes | Engine operating time in hours for G19
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_EngineRuntime_VAL | Yes | Engine operating time in hours for G20
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_EngineRuntime_VAL | Yes | Engine operating time in hours for G21
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_EngineRuntime_VAL | Yes | Engine operating time in hours for G22
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_EngineRuntime_VAL | Yes | Engine operating time in hours for G23
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_EngineRuntime_VAL | Yes | Engine operating time in hours for G24
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_EngineRuntime_VAL | Yes | Engine operating time in hours for G25
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_EngineRuntime_VAL | Yes | Engine operating time in hours for G26
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_EngineRuntime_VAL | Yes | Engine operating time in hours for G27
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_EngineRuntime_VAL | Yes | Engine operating time in hours for G28
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_EngineRuntime_VAL | Yes | Engine operating time in hours for G29
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_EngineRuntime_VAL | Yes | Engine operating time in hours for G30
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_EngineRuntime_VAL | Yes | Engine operating time in hours for G31
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_EngineRuntime_VAL | Yes | Engine operating time in hours for G32
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_EngineRuntime_VAL | Yes | Engine operating time in hours for G33
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_EngineRuntime_VAL | Yes | Engine operating time in hours for G34
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_EngineRuntime_VAL | Yes | Engine operating time in hours for G35
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_EngineRuntime_VAL | Yes | Engine operating time in hours for G36
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_EngineRuntime_VAL | Yes | Engine operating time in hours for G37
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_EngineRuntime_VAL | Yes | Engine operating time in hours for G38
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_EngineRuntime_VAL | Yes | Engine operating time in hours for G39
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_EngineRuntime_VAL | Yes | Engine operating time in hours for G40
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_EngineRuntime_VAL | Yes | Engine operating time in hours for G41
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_EngineRuntime_VAL | Yes | Engine operating time in hours for G42
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_EngineRuntime_VAL | Yes | Engine operating time in hours for G43
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_EngineRuntime_VAL | Yes | Engine operating time in hours for G44
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_EngineRuntime_VAL | Yes | Engine operating time in hours for G45
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_EngineRuntime_VAL | Yes | Engine operating time in hours for G46
Generation Management Control Screens | QPAC-1 | GEN1 | GCS_G1_SpinningReserve_VAL | Yes | Spinning reserve for G1
Generation Management Control Screens | QPAC-1 | GEN2 | GCS_G2_SpinningReserve_VAL | Yes | Spinning reserve for G2
Generation Management Control Screens | QPAC-1 | GEN3 | GCS_G3_SpinningReserve_VAL | Yes | Spinning reserve for G3
Generation Management Control Screens | QPAC-1 | GEN4 | GCS_G4_SpinningReserve_VAL | Yes | Spinning reserve for G4
Generation Management Control Screens | QPAC-2 | GEN5 | GCS_G5_SpinningReserve_VAL | Yes | Spinning reserve for G5
Generation Management Control Screens | QPAC-2 | GEN6 | GCS_G6_SpinningReserve_VAL | Yes | Spinning reserve for G6
Generation Management Control Screens | QPAC-2 | GEN7 | GCS_G7_SpinningReserve_VAL | Yes | Spinning reserve for G7
Generation Management Control Screens | QPAC-2 | GEN8 | GCS_G8_SpinningReserve_VAL | Yes | Spinning reserve for G8
Generation Management Control Screens | QPAC-3 | GEN9 | GCS_G9_SpinningReserve_VAL | Yes | Spinning reserve for G9
Generation Management Control Screens | QPAC-3 | GEN10 | GCS_G10_SpinningReserve_VAL | Yes | Spinning reserve for G10
Generation Management Control Screens | QPAC-3 | GEN11 | GCS_G11_SpinningReserve_VAL | Yes | Spinning reserve for G11
Generation Management Control Screens | QPAC-3 | GEN12 | GCS_G12_SpinningReserve_VAL | Yes | Spinning reserve for G12
Generation Management Control Screens | QPAC-4 | GEN13 | GCS_G13_SpinningReserve_VAL | Yes | Spinning reserve for G13
Generation Management Control Screens | QPAC-4 | GEN14 | GCS_G14_SpinningReserve_VAL | Yes | Spinning reserve for G14
Generation Management Control Screens | QPAC-4 | GEN15 | GCS_G15_SpinningReserve_VAL | Yes | Spinning reserve for G15
Generation Management Control Screens | QPAC-4 | GEN16 | GCS_G16_SpinningReserve_VAL | Yes | Spinning reserve for G16
Generation Management Control Screens | QPAC-5 | GEN17 | GCS_G17_SpinningReserve_VAL | Yes | Spinning reserve for G17
Generation Management Control Screens | QPAC-5 | GEN18 | GCS_G18_SpinningReserve_VAL | Yes | Spinning reserve for G18
Generation Management Control Screens | QPAC-5 | GEN19 | GCS_G19_SpinningReserve_VAL | Yes | Spinning reserve for G19
Generation Management Control Screens | QPAC-5 | GEN20 | GCS_G20_SpinningReserve_VAL | Yes | Spinning reserve for G20
Generation Management Control Screens | QPAC-6 | GEN21 | GCS_G21_SpinningReserve_VAL | Yes | Spinning reserve for G21
Generation Management Control Screens | QPAC-6 | GEN22 | GCS_G22_SpinningReserve_VAL | Yes | Spinning reserve for G22
Generation Management Control Screens | QPAC-6 | GEN23 | GCS_G23_SpinningReserve_VAL | Yes | Spinning reserve for G23
Generation Management Control Screens | QPAC-6 | GEN24 | GCS_G24_SpinningReserve_VAL | Yes | Spinning reserve for G24
Generation Management Control Screens | QPAC-7 | GEN25 | GCS_G25_SpinningReserve_VAL | Yes | Spinning reserve for G25
Generation Management Control Screens | QPAC-7 | GEN26 | GCS_G26_SpinningReserve_VAL | Yes | Spinning reserve for G26
Generation Management Control Screens | QPAC-7 | GEN27 | GCS_G27_SpinningReserve_VAL | Yes | Spinning reserve for G27
Generation Management Control Screens | QPAC-7 | GEN28 | GCS_G28_SpinningReserve_VAL | Yes | Spinning reserve for G28
Generation Management Control Screens | QPAC-8 | GEN29 | GCS_G29_SpinningReserve_VAL | Yes | Spinning reserve for G29
Generation Management Control Screens | QPAC-8 | GEN30 | GCS_G30_SpinningReserve_VAL | Yes | Spinning reserve for G30
Generation Management Control Screens | QPAC-8 | GEN31 | GCS_G31_SpinningReserve_VAL | Yes | Spinning reserve for G31
Generation Management Control Screens | QPAC-8 | GEN32 | GCS_G32_SpinningReserve_VAL | Yes | Spinning reserve for G32
Generation Management Control Screens | QPAC-9 | GEN33 | GCS_G33_SpinningReserve_VAL | Yes | Spinning reserve for G33
Generation Management Control Screens | QPAC-9 | GEN34 | GCS_G34_SpinningReserve_VAL | Yes | Spinning reserve for G34
Generation Management Control Screens | QPAC-9 | GEN35 | GCS_G35_SpinningReserve_VAL | Yes | Spinning reserve for G35
Generation Management Control Screens | QPAC-9 | GEN36 | GCS_G36_SpinningReserve_VAL | Yes | Spinning reserve for G36
Generation Management Control Screens | QPAC-10 | GEN37 | GCS_G37_SpinningReserve_VAL | Yes | Spinning reserve for G37
Generation Management Control Screens | QPAC-10 | GEN38 | GCS_G38_SpinningReserve_VAL | Yes | Spinning reserve for G38
Generation Management Control Screens | QPAC-10 | GEN39 | GCS_G39_SpinningReserve_VAL | Yes | Spinning reserve for G39
Generation Management Control Screens | QPAC-10 | GEN40 | GCS_G40_SpinningReserve_VAL | Yes | Spinning reserve for G40
Generation Management Control Screens | QPAC-11 | GEN41 | GCS_G41_SpinningReserve_VAL | Yes | Spinning reserve for G41
Generation Management Control Screens | QPAC-11 | GEN42 | GCS_G42_SpinningReserve_VAL | Yes | Spinning reserve for G42
Generation Management Control Screens | QPAC-11 | GEN43 | GCS_G43_SpinningReserve_VAL | Yes | Spinning reserve for G43
Generation Management Control Screens | QPAC-11 | GEN44 | GCS_G44_SpinningReserve_VAL | Yes | Spinning reserve for G44
Generation Management Control Screens | QPAC-12 | GEN45 | GCS_G45_SpinningReserve_VAL | Yes | Spinning reserve for G45
Generation Management Control Screens | QPAC-12 | GEN46 | GCS_G46_SpinningReserve_VAL | Yes | Spinning reserve for G46
Automatic Generation Control Screens | QPAC-1 | GEN1 | AGC_G1_Frequency_VAL | Yes | Frequency (Hz) from field for G1
Automatic Generation Control Screens | QPAC-1 | GEN2 | AGC_G2_Frequency_VAL | Yes | Frequency (Hz) from field for G2
Automatic Generation Control Screens | QPAC-1 | GEN3 | AGC_G3_Frequency_VAL | Yes | Frequency (Hz) from field for G3
Automatic Generation Control Screens | QPAC-1 | GEN4 | AGC_G4_Frequency_VAL | Yes | Frequency (Hz) from field for G4
Automatic Generation Control Screens | QPAC-2 | GEN5 | AGC_G5_Frequency_VAL | Yes | Frequency (Hz) from field for G5
Automatic Generation Control Screens | QPAC-2 | GEN6 | AGC_G6_Frequency_VAL | Yes | Frequency (Hz) from field for G6
Automatic Generation Control Screens | QPAC-2 | GEN7 | AGC_G7_Frequency_VAL | Yes | Frequency (Hz) from field for G7
Automatic Generation Control Screens | QPAC-2 | GEN8 | AGC_G8_Frequency_VAL | Yes | Frequency (Hz) from field for G8
Automatic Generation Control Screens | QPAC-3 | GEN9 | AGC_G9_Frequency_VAL | Yes | Frequency (Hz) from field for G9
Automatic Generation Control Screens | QPAC-3 | GEN10 | AGC_G10_Frequency_VAL | Yes | Frequency (Hz) from field for G10
Automatic Generation Control Screens | QPAC-3 | GEN11 | AGC_G11_Frequency_VAL | Yes | Frequency (Hz) from field for G11
Automatic Generation Control Screens | QPAC-3 | GEN12 | AGC_G12_Frequency_VAL | Yes | Frequency (Hz) from field for G12
Automatic Generation Control Screens | QPAC-4 | GEN13 | AGC_G13_Frequency_VAL | Yes | Frequency (Hz) from field for G13
Automatic Generation Control Screens | QPAC-4 | GEN14 | AGC_G14_Frequency_VAL | Yes | Frequency (Hz) from field for G14
Automatic Generation Control Screens | QPAC-4 | GEN15 | AGC_G15_Frequency_VAL | Yes | Frequency (Hz) from field for G15
Automatic Generation Control Screens | QPAC-4 | GEN16 | AGC_G16_Frequency_VAL | Yes | Frequency (Hz) from field for G16
Automatic Generation Control Screens | QPAC-5 | GEN17 | AGC_G17_Frequency_VAL | Yes | Frequency (Hz) from field for G17
Automatic Generation Control Screens | QPAC-5 | GEN18 | AGC_G18_Frequency_VAL | Yes | Frequency (Hz) from field for G18
Automatic Generation Control Screens | QPAC-5 | GEN19 | AGC_G19_Frequency_VAL | Yes | Frequency (Hz) from field for G19
Automatic Generation Control Screens | QPAC-5 | GEN20 | AGC_G20_Frequency_VAL | Yes | Frequency (Hz) from field for G20
Automatic Generation Control Screens | QPAC-6 | GEN21 | AGC_G21_Frequency_VAL | Yes | Frequency (Hz) from field for G21
Automatic Generation Control Screens | QPAC-6 | GEN22 | AGC_G22_Frequency_VAL | Yes | Frequency (Hz) from field for G22
Automatic Generation Control Screens | QPAC-6 | GEN23 | AGC_G23_Frequency_VAL | Yes | Frequency (Hz) from field for G23
Automatic Generation Control Screens | QPAC-6 | GEN24 | AGC_G24_Frequency_VAL | Yes | Frequency (Hz) from field for G24
Automatic Generation Control Screens | QPAC-7 | GEN25 | AGC_G25_Frequency_VAL | Yes | Frequency (Hz) from field for G25
Automatic Generation Control Screens | QPAC-7 | GEN26 | AGC_G26_Frequency_VAL | Yes | Frequency (Hz) from field for G26
Automatic Generation Control Screens | QPAC-7 | GEN27 | AGC_G27_Frequency_VAL | Yes | Frequency (Hz) from field for G27
Automatic Generation Control Screens | QPAC-7 | GEN28 | AGC_G28_Frequency_VAL | Yes | Frequency (Hz) from field for G28
Automatic Generation Control Screens | QPAC-8 | GEN29 | AGC_G29_Frequency_VAL | Yes | Frequency (Hz) from field for G29
Automatic Generation Control Screens | QPAC-8 | GEN30 | AGC_G30_Frequency_VAL | Yes | Frequency (Hz) from field for G30
Automatic Generation Control Screens | QPAC-8 | GEN31 | AGC_G31_Frequency_VAL | Yes | Frequency (Hz) from field for G31
Automatic Generation Control Screens | QPAC-8 | GEN32 | AGC_G32_Frequency_VAL | Yes | Frequency (Hz) from field for G32
Automatic Generation Control Screens | QPAC-9 | GEN33 | AGC_G33_Frequency_VAL | Yes | Frequency (Hz) from field for G33
Automatic Generation Control Screens | QPAC-9 | GEN34 | AGC_G34_Frequency_VAL | Yes | Frequency (Hz) from field for G34
Automatic Generation Control Screens | QPAC-9 | GEN35 | AGC_G35_Frequency_VAL | Yes | Frequency (Hz) from field for G35
Automatic Generation Control Screens | QPAC-9 | GEN36 | AGC_G36_Frequency_VAL | Yes | Frequency (Hz) from field for G36
Automatic Generation Control Screens | QPAC-10 | GEN37 | AGC_G37_Frequency_VAL | Yes | Frequency (Hz) from field for G37
Automatic Generation Control Screens | QPAC-10 | GEN38 | AGC_G38_Frequency_VAL | Yes | Frequency (Hz) from field for G38
Automatic Generation Control Screens | QPAC-10 | GEN39 | AGC_G39_Frequency_VAL | Yes | Frequency (Hz) from field for G39
Automatic Generation Control Screens | QPAC-10 | GEN40 | AGC_G40_Frequency_VAL | Yes | Frequency (Hz) from field for G40
Automatic Generation Control Screens | QPAC-11 | GEN41 | AGC_G41_Frequency_VAL | Yes | Frequency (Hz) from field for G41
Automatic Generation Control Screens | QPAC-11 | GEN42 | AGC_G42_Frequency_VAL | Yes | Frequency (Hz) from field for G42
Automatic Generation Control Screens | QPAC-11 | GEN43 | AGC_G43_Frequency_VAL | Yes | Frequency (Hz) from field for G43
Automatic Generation Control Screens | QPAC-11 | GEN44 | AGC_G44_Frequency_VAL | Yes | Frequency (Hz) from field for G44
Automatic Generation Control Screens | QPAC-12 | GEN45 | AGC_G45_Frequency_VAL | Yes | Frequency (Hz) from field for G45
Automatic Generation Control Screens | QPAC-12 | GEN46 | AGC_G46_Frequency_VAL | Yes | Frequency (Hz) from field for G46
Voltage Control System Screens | QPAC-1 | GEN1 | VCS_G1_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN1
Voltage Control System Screens | QPAC-1 | GEN2 | VCS_G2_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN2
Voltage Control System Screens | QPAC-1 | GEN3 | VCS_G3_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN3
Voltage Control System Screens | QPAC-1 | GEN4 | VCS_G4_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN4
Voltage Control System Screens | QPAC-2 | GEN5 | VCS_G5_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN5
Voltage Control System Screens | QPAC-2 | GEN6 | VCS_G6_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN6
Voltage Control System Screens | QPAC-2 | GEN7 | VCS_G7_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN7
Voltage Control System Screens | QPAC-2 | GEN8 | VCS_G8_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN8
Voltage Control System Screens | QPAC-3 | GEN9 | VCS_G9_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN9
Voltage Control System Screens | QPAC-3 | GEN10 | VCS_G10_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN10
Voltage Control System Screens | QPAC-3 | GEN11 | VCS_G11_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN11
Voltage Control System Screens | QPAC-3 | GEN12 | VCS_G12_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN12
Voltage Control System Screens | QPAC-4 | GEN13 | VCS_G13_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN13
Voltage Control System Screens | QPAC-4 | GEN14 | VCS_G14_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN14
Voltage Control System Screens | QPAC-4 | GEN15 | VCS_G15_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN15
Voltage Control System Screens | QPAC-4 | GEN16 | VCS_G16_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN16
Voltage Control System Screens | QPAC-5 | GEN17 | VCS_G17_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN17
Voltage Control System Screens | QPAC-5 | GEN18 | VCS_G18_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN18
Voltage Control System Screens | QPAC-5 | GEN19 | VCS_G19_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN19
Voltage Control System Screens | QPAC-5 | GEN20 | VCS_G20_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN20
Voltage Control System Screens | QPAC-6 | GEN21 | VCS_G21_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN21
Voltage Control System Screens | QPAC-6 | GEN22 | VCS_G22_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN22
Voltage Control System Screens | QPAC-6 | GEN23 | VCS_G23_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN23
Voltage Control System Screens | QPAC-6 | GEN24 | VCS_G24_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN24
Voltage Control System Screens | QPAC-7 | GEN25 | VCS_G25_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN25
Voltage Control System Screens | QPAC-7 | GEN26 | VCS_G26_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN26
Voltage Control System Screens | QPAC-7 | GEN27 | VCS_G27_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN27
Voltage Control System Screens | QPAC-7 | GEN28 | VCS_G28_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN28
Voltage Control System Screens | QPAC-8 | GEN29 | VCS_G29_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN29
Voltage Control System Screens | QPAC-8 | GEN30 | VCS_G30_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN30
Voltage Control System Screens | QPAC-8 | GEN31 | VCS_G31_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN31
Voltage Control System Screens | QPAC-8 | GEN32 | VCS_G32_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN32
Voltage Control System Screens | QPAC-9 | GEN33 | VCS_G33_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN33
Voltage Control System Screens | QPAC-9 | GEN34 | VCS_G34_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN34
Voltage Control System Screens | QPAC-9 | GEN35 | VCS_G35_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN35
Voltage Control System Screens | QPAC-9 | GEN36 | VCS_G36_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN36
Voltage Control System Screens | QPAC-10 | GEN37 | VCS_G37_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN37
Voltage Control System Screens | QPAC-10 | GEN38 | VCS_G38_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN38
Voltage Control System Screens | QPAC-10 | GEN39 | VCS_G39_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN39
Voltage Control System Screens | QPAC-10 | GEN40 | VCS_G40_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN40
Voltage Control System Screens | QPAC-11 | GEN41 | VCS_G41_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN41
Voltage Control System Screens | QPAC-11 | GEN42 | VCS_G42_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN42
Voltage Control System Screens | QPAC-11 | GEN43 | VCS_G43_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN43
Voltage Control System Screens | QPAC-11 | GEN44 | VCS_G44_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN44
Voltage Control System Screens | QPAC-12 | GEN45 | VCS_G45_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN45
Voltage Control System Screens | QPAC-12 | GEN46 | VCS_G46_ReactivePower_VAL | Yes | Reactive power (MVAR) from field for GEN46